## README
General Notes:
1 | This electronic CIP (eCIP) was created to summarize the updated CIP projects, as defined in the Willamette River Water Treatment Plant - 2017 Master Plan Update (Carollo, March 2018)
2 | The eCIP content falls within one of three categories, represented by tab color:
Red tabs represent Work where the User can enter values.
Green tabs summarize project details, including scope, schedule and fee, and are paginated for easy printing.
Purple tabs summarize financial information in either tabular or graphical format.
3 | This eCIP calculates the CIP costs within the planning horizon by allocating project costs between construction start/end dates.
4 | Workbook is protected to prevent user from accidentally editing formulas. Password to remove protection is "MPU2017"
5 | Need Help? Please contact Carollo Engineers at 503.227.1885 for assistance.
Worksheet Summary:
ReadMe
Provides instructions on how to use the workbook as well as a list of user-inputed variables.
CIP Summary
Provides a general overview of the eCIP, including input variables. Also, primarily used to enter values for project cost and schedule.
CIP Full
Provides a detailed summary of the eCIP projects and all associated project tasks.
Project Sheets (P1 - P5)
Provides a project summary for individual projects. These worksheets have been organized to be 'printer friendly',
allowing the User to quickly print a brief summary of project scope and schedule. Projects include:
P1 - 20 MGD Expansion
P2 - Life-safety Repairs
P3 - Seismic Retrofits
P4 - 30 MGD Capacity Expansion
P5 - Ongoing Repair and Replacement Activities
Stakeholder Categories
Defines the costsharing breakdown between stakeholders, including basis, caveats, and review cycle.
Financial Summary (2017)
Provides a summary of the CIP financials in 2017 dollars, including: total and individual agency costs/fiscal year, total project costs
costsby project and city.
Financial Summary (Future)
Provides a summary of the CIP financials in projected future dollars, including: total and individual agency costs/fiscal year, total project
by project and city.
Charts
Provides a visual summary of the total CIP costs (in 2017 dollars) for the near-term (FY 2018 - 2022) and long-term (FY 2018 - 2036) based on CIP project and stakeholder.
Input Variables:
General Notes:
Red cells/values can be changed to update the CIP.
Black cells are automatically calculated and should not be changed.
| Varible | Worksheet | Comments
| Type of Cost Projection | CIP Summary | Determines if cost projection is based on ENR, Escalation, or Revised ENR
| Project Completion Year | CIP Summary | The year when the project should be completed
| Project Duration | CIP Summary | Allows the user to override the calculated project duration (based on design,
construction, and float) and instead use a user-entered value, in years
| Design Duration | CIP Summary | Assumed design duration, in months
| Construction Duration | CIP Summary | Assumed construction duration, in months
| Schedule Float | CIP Summary | Assumed schedule float, in months
| Estimated Project Cost | CIP Full | Can be revised to reflect change in total cost of work for the task
| Design Project? | CIP Full | Determines whether project duration should include design phase or is
construction only
General Assumptions:
| Escalation Rate | 1.03 | (Example: 1.03 = 3% inflation rate. Enter 1.00 for 2017 Dollars)
| Estimate Date | 2017-09-01 | (Date CIP estimate was generated. Format: mm/dd/yyyy)
| ENR @ Date | 10823 | (20-City Average ENR at the listed estimate date)
| Design Contingency | 15% | (For Engineering Design)
| Admin Contingency | 10% | (For Legal and Administration)
| Revised Estimate Date | 2017-09-01 | (If revising the estimate table to a new date. Format: mm/dd/yyyy)
| ENR @ Revised Estimate Date | 10823 | (ENR at the revised estimate date)
| Responsibility Category |  |  |  | Wilsonville Split
| Project | Category | City of Wilsonville | City of Sherwood | SDCs | Rates
| 20 MGD Expansion | 1 | 66.7% | 33.3% | 42% | 25%
| Life Safety Repairs | 1 | 66.7% | 33.3%
| Seismic Retrofits | 1 | 66.7% | 33.3%
| 30 MGD Expansion | 2 | 67.7% | 32.3%
| Repair & Replace | 1 | 66.7% | 33.3%
CIP Column Notes:
This section lists the purpose of each column header in CIP Summary and CIP Full. This list of notes is intended for the user's reference
when using a hardcopy file.
| Column Header | Sheet | User-Entered Field? | Comment/Instructions
| CIP Project Stage | CIP Summary & CIP Full | No | Project name. Each ties into individual project sheets P1 to P5.
| Type of Cost Projection | CIP Summary | Yes | If "Escalation", project costs are calculated using escalation rate selected on this sheet. If "Revised ENR", project costs are calculated using ratio of "ENR @ Date" and "ENR @ Revised Estimate Date" and escalation rate beyond "Revised Estimate Date".
| Estimated Construction Cost | CIP Summary | No (CIP Summary) / Yes(CIP Full) | Estimated Construction Cost from OPCC and Cost Factoring Workbook. To edit estimate construction cost for individual project tasks, go to "CIP Full" sheet.
| Design + Admin Cost | CIP Summary | No | Estimated design and adminstrative costs based on Estimated construction cost and design and adminstrative contingency.
| Total Estimated Project Cost | CIP Summary & CIP Full | No | Sum of Construction, Design, and Adminstrative Costs
| Project Completion Year | CIP Summary | Yes | Estimated year that project comes online. User Entered value in CIP Summary
| ENR @ Project Year | CIP Summary | Yes | ENR value at project completion year. User entered value.
| Future Value in Approx. Project Year | CIP Summary & CIP Full | No | Future value of project based on assumed escalation rate, ENR, or Revised ENR based on user selection
| Project Duration | CIP Summary | No | Assumed Project Duration based on Design Duration, Construction Duration, and Schedule Float
| Project Duration (red) | CIP Summary | Yes | Use this column to manually change project duration. If not manually changing project duration, value in cell must be "0"
| Project Start Year | CIP Summary | No | Calculated project start year based on design, construction, and float durations (or user-entered project duration)
| Design Duration | CIP Summary | Yes | Assumed duration of project design in months
| Construction Duration | CIP Summary | Yes | Assumed duration of project construction in months
| Schedule Float | CIP Summary | Yes | Assumed project float in months
| Design Start | CIP Summary | Yes | Design start date caluclated based on Assumed Project Year, Design Duration, Construction Duration, and Float.
| Construction Start | CIP Summary | Yes | Construction start date caluclated based on Assumed Project Year, Construction Duration, and Float.
| Actual Project Cost | CIP Summary | Yes | Sums actual construction costs that were entered on project sheets.
| P# | CIP Full | No | Project number that ties back to estimate source for ease of updating.
| System Name | CIP Full | No | Identifies WTP plant system assocaited with task
| CIP - Task Description | CIP Full | No | Description of task scope used to develop estimate.
| Estimated Construction Cost | CIP Full | Yes | Estimated Construction Cost from OPCC and Cost Factoring Workbook.
| Design Project? | CIP Full | Yes | Yes - Design and Admin Contingency added; No - Only Admin Contingency added
| Estimated Design Cost | CIP Full | No | Calculated design cost based on project construction cost and design escalation rate. Value is $0 if Design Project field = No.
| Estimated Adminstrative Cost | CIP Full | No | Calculated adminstrative cost based on project construction cost and adminstration escalation rate.
| Future Design Cost | CIP Full | No | Future design cost based on assumed escalation rate, ENR, or Revised ENR based on user selection
| Future Adminstrative Cost | CIP Full | No | Future administrative cost based on assumed escalation rate, ENR, or Revised ENR based on user selection
| Design Start | CIP Full | Yes | Design start date caluclated based on Assumed Project Year, Design Duration, Construction Duration, and Float. R&R Tasks can be edited.
| Construction Start | CIP Full | Yes | Construction start date caluclated based on Assumed Project Year, Construction Duration, and Float. R&R Tasks can be edited.

## CIP Summary
Willamette River Water Treatment Plant - 2017 Master Plan Update
Capital Improvement Projects Summary
CIP SUMMARY TABLE
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
CIP Project Stage # | CIP Project Stage | Type of Cost Projection | Estimated Construction Cost | Design + Admin Cost | Total Estimated Project Cost(1) | Project Completion Year | ENR @ Project Year | Future Value in Project Year - Escalation | Project Duration (Years) | Project Duration (Years) | Project Start Year | Design Duration (Months) | Construction Duration (Months) | Schedule Float (Months) | Design Start | Construction Start | Actual Project Cost
1 | 20 MGD Expansion | Escalation | 12580000 | 3150000 | 15730000 | 2021 |  | 17710000 | 3 | 0 | 2018 | 12 | 18 | 6 | 2018 | 2019 | 0
2 | Life-Safety Repairs | Escalation | 570000 | 60000 | 630000 | 2022 |  | 720000 | 2 | 0 | 2020 | 6 | 6 | 3 | 2020 | 2021 | 0
3 | Seismic Retrofits | Escalation | 930000 | 240000 | 1170000 | 2022 |  | 1340000 | 2 | 0 | 2020 | 6 | 6 | 3 | 2020 | 2021 | 0
4 | 30 MGD Expansion | Escalation | 30920000 | 7730000 | 38650000 | 2034 |  | 63870000 | 4 | 0 | 2030 | 12 | 24 | 6 | 2030 | 2031 | 0
| TOTAL COSTS |  | 45020000 | 11170000 | 56190000
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
(2) | All costs in the CIP Summary table are rounded up to nearest $10,000. For more detailed costs, see the CIP Full table.
Ongoing Repair and Replacement Activities Summary (by Project Completion Year)
Type of Cost Projection |  | Escalation
Construction Duration (months) |  | 6
Schedule Float (months) |  | 6
CIP Project Stage # | CIP Project Stage | Year | ENR @ Project Year | Estimated Construction Cost | Etimated Administrative Cost | Estimated Task Cost(1) | Future Value in Project Year - Escalation | Admin Cost in Project Year - Escalation | Construction Cost in Project Year - Escalation | Actual Project Cost
5 | Repair & Replace - Year 1 | 2019 |  | 1360000 | 140000 | 1500000 | 1590000 | 160000 | 1430000 | 0
5 | Repair & Replace - Year 2 | 2020 |  | 1450000 | 150000 | 1600000 | 1740000 | 180000 | 1560000 | 0
5 | Repair & Replace - Year 3 | 2021 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 4 | 2022 |  | 3110000 | 320000 | 3430000 | 3970000 | 400000 | 3570000 | 0
5 | Repair & Replace - Year 5 | 2023 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 6 | 2024 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 7 | 2025 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 8 | 2026 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 9 | 2027 |  | 4740000 | 480000 | 5220000 | 7010000 | 710000 | 6300000 | 0
5 | Repair & Replace - Year 10 | 2028 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 11 | 2029 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 12 | 2030 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 13 | 2031 |  | 20000 | 10000 | 30000 | 20000 | 10000 | 10000 | 0
5 | Repair & Replace - Year 14 | 2032 |  | 2260000 | 230000 | 2490000 | 3860000 | 390000 | 3470000 | 0
5 | Repair & Replace - Year 15 | 2033 |  | 20000 | 10000 | 30000 | 30000 | 10000 | 20000 | 0
5 | Repair & Replace - Year 16 | 2034 |  | 20000 | 10000 | 30000 | 30000 | 10000 | 20000 | 0
5 | Repair & Replace - Year 17 | 2035 |  | 20000 | 10000 | 30000 | 30000 | 10000 | 20000 | 0
5 | Repair & Replace - Year 18 | 2036 |  | 3090000 | 310000 | 3400000 | 5960000 | 600000 | 5360000 | 0
5 | Repair & Replace Total |  |  | 16130000 | 1610000 | 17740000 | 24400000 | 2560000 | 21840000 | 0
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
(2) | All costs in the CIP Summary table are rounded up to nearest $10,000. For more detailed costs, see the CIP Full table.
Note on B7: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C7: Natalie Reilly: If "Escalation", project costs are calculated using escalation rate selected on this sheet. If "Revised ENR", project costs are calculated using ratio of "ENR @ Date" and "ENR @ Revised Estimate Date" and escalation rate beyond "Revised Estimate Date".
Note on D7: Natalie Reilly: To edit estimate construction cost for individual project tasks, go to "CIP Full" sheet. Estimated Construction Cost from OPCC and Cost Factoring Workbook.
Note on E7: Meghann Chell: Estimated design and adminstrative costs based on Estimated construction cost and design and adminstrative contingency.
Note on F7: Meghann Chell: Sum of Construction, Design, and Adminstrative Costs
Note on G7: Meghann Chell: Estimated year that project comes online. User entered value in CIP Summary
Note on H7: Meghann Chell: ENR value at project completion year. User entered value.
Note on I7: Meghann Chell: Future value of project based on assumed escalation rate.
Note on J7: Natalie Reilly: Assumed Project Duration based on Design Duration, Construction Duration, and Schedule Float.
Note on K7: Natalie Reilly: Use this column to manually change project duration. If not manually changing project duration, value in cell must be "0".
Note on L7: Meghann Chell: Calculated project start year based on design, construction, and float durations (or user-entered project duration)
Note on M7: Natalie Reilly: Assumed duration of project design.
Note on N7: Natalie Reilly: Assumed duration of project construction.
Note on O7: Natalie Reilly: Assumed project float.
Note on P7: Natalie Reilly: Design start date caluclated based on Assumed Project Year, Design Duration, Construction Duration, and Float.
Note on Q7: Natalie Reilly: Construction start date caluclated based on Assumed Project Year, Construction Duration, and Float.
Note on R7: Natalie Reilly: Sums actual construction costs that were entered on project sheets.
Note on A21: Natalie Reilly: If "Escalation", project costs are calculated using escalation rate selected on this sheet. If "Revised ENR", project costs are calculated using ratio of "ENR @ Date" and "ENR @ Revised Estimate Date" and escalation rate beyond "Revised Estimate Date".
Note on B25: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C25: Meghann Chell: Estimated year that project comes online. Editable in CIP Full sheet for individual tasks.
Note on E25: Natalie Reilly: To edit estimate construction cost for individual project tasks, go to "CIP Full" sheet. Estimated Construction Cost from OPCC and Cost Factoring Workbook.
Note on H25: Meghann Chell: Future value of project based on assumed escalation rate.
Note on K25: Natalie Reilly: Sums actual construction costs that were entered on project sheets.

## CIP Full
Willamette River Water Treatment Plant - 2017 Master Plan Update
Capital Improvement Projects Summary
DETAIL CIP SUMMARY
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Type of Cost Projection | Estimated Design Cost | Estimated Administrative Cost | Estimated Total Cost(1) | Project Completion Year | ENR @ Project Year | Future Value in Project Year - Escalation | Future Design Cost - Escalation | Future Administrative Cost - Escalation | Design Duration (Months) | Construction Duration (Months) | Schedule Float (Months) | Design Start | Construction Start
1 | 20 MGD Expansion | Actiflo™ | Install second flash mix pump to give system installed redundancy (1+1) rather than shelf spare. | 169791 | Yes | Escalation | 25468.65 | 16979.1 | 212238.75 | 2021 | 0 | 238876.5829 | 28665.19 | 19110.1266 | 12 | 18 | 6 | 2018 | 2019
2 | 20 MGD Expansion | Actiflo™ | Purchase additional shelf spare solid pump | 42275 | Yes | Escalation | 6341.25 | 4227.5 | 52843.75 | 2021 | 0 | 59476.1062 | 7137.1327 | 4758.0885 | 12 | 18 | 6 | 2018 | 2019
3 | 30 MGD Expansion | Actiflo™ | Construct an additional Actiflo basin for the 30 MGD capacity upgrade. With the addition of a third basin, the WRWTP will have three 10 MGD basins and can run two basins at 15 MGD in the event one basin requires maintenance. | 4864843 | Yes | Escalation | 729726.45 | 486484.3 | 6081053.75 | 2034 | 0 | 10051055.2924 | 1206126.6351 | 804084.4234 | 12 | 24 | 6 | 2030 | 2031
4 | Life-Safety Repairs | Actiflo™ | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | Escalation | 0 | 642.7 | 7069.7 | 2022 | 0 | 8195.7199 | 0 | 745.0654 | 6 | 6 | 3 | 2020 | 2021
5 | Life-Safety Repairs | Actiflo™ | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 36136 | No | Escalation | 0 | 3613.6 | 39749.6 | 2022 | 0 | 46080.6807 | 0 | 4189.1528 | 6 | 6 | 3 | 2020 | 2021
6 | Life-Safety Repairs | Actiflo™ | The rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | Escalation | 0 | 701.1 | 7712.1 | 2022 | 0 | 8940.4376 | 0 | 812.7671 | 6 | 6 | 3 | 2020 | 2021
7 | Life-Safety Repairs | Actiflo™ | The west guardrail on top of the Actiflo™ tanks does not have continuous kickplates. Install new kickplates as required. (LS8) | 2305 | No | Escalation | 0 | 230.5 | 2535.5 | 2022 | 0 | 2939.3394 | 0 | 267.2127 | 6 | 6 | 3 | 2020 | 2021
8 | Life-Safety Repairs | Actiflo™ | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 2425 | No | Escalation | 0 | 242.5 | 2667.5 | 2022 | 0 | 3092.3636 | 0 | 281.124 | 6 | 6 | 3 | 2020 | 2021
9 | Life-Safety Repairs | Actiflo™ | The doors were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required at Actiflo™ building. (LS7) | 33171 | No | Escalation | 0 | 3317.1 | 36488.1 | 2022 | 0 | 42299.7084 | 0 | 3845.428 | 6 | 6 | 3 | 2020 | 2021
10 | Repair & Replace | Actiflo™ | Replace the four hydrocyclones installed in the two existing Actiflo Basins | 318000 | No | Escalation | 0 | 31800 | 349800 | 2020 | 0 | 382235.9046 | 0 | 34748.7186 | 0 | 6 | 6 | 2019 | 2019
11 | 20 MGD Expansion | Actiflo™ | Replace and reinstall existing streaming current analyzer on Actiflo inlet so it can be used for chemical dosing | 70500 | Yes | Escalation | 10575 | 7050 | 88125 | 2020 | 0 | 96296.5669 | 11555.588 | 7703.7253 | 12 | 18 | 6 | 2017 | 2018
12 | Repair & Replace | Actiflo™ | Replace lamella settling tubes in the two existing Actiflo basins, which are damaged due to UV exposure. | 245656 | No | Escalation | 0 | 24565.6 | 270221.6 | 2020 | 0 | 295278.4383 | 0 | 26843.4944 | 0 | 6 | 6 | 2019 | 2019
13 | Repair & Replace | Actiflo™ | Upgrade vendor PLC components in the two existing Actiflo basins | 62108 | No | Escalation | 0 | 6210.8 | 68318.8 | 2022 | 0 | 79200.2136 | 0 | 7200.0194 | 0 | 6 | 6 | 2021 | 2021
14 | Repair & Replace | Actiflo™ | Replace the two flash mix pumps (installed and standby) | 188760 | No | Escalation | 0 | 18876 | 207636 | 2020 | 0 | 226889.4634 | 0 | 20626.3149 | 0 | 6 | 6 | 2019 | 2019
15 | Repair & Replace | Actiflo™ | Replace the six mixers installed in the two existing Actiflo Basins | 302400 | No | Escalation | 0 | 30240 | 332640 | 2022 | 0 | 385620.9281 | 0 | 35056.448 | 0 | 6 | 6 | 2021 | 2021
16 | Repair & Replace | Actiflo™ | Replace the two sample pumps installed in the two existing Actiflo Basins | 46051 | No | Escalation | 0 | 4605.1 | 50656.1 | 2022 | 0 | 58724.3034 | 0 | 5338.573 | 0 | 6 | 6 | 2021 | 2021
17 | Repair & Replace | Actiflo™ | Replace original dry polymer batching system (T-13ME01) | 198750 | No | Escalation | 0 | 19875 | 218625 | 2027 | 0 | 293813.7184 | 0 | 26710.338 | 0 | 6 | 6 | 2026 | 2026
18 | Repair & Replace | Actiflo™ | PLC upgrade for Actiflo Local Control Panels | 84000 | No | Escalation | 0 | 8400 | 92400 | 2027 | 0 | 124177.8735 | 0 | 11288.8976 | 0 | 6 | 6 | 2026 | 2026
19 | Repair & Replace | Actiflo™ | Replace existing streaming current analyzer on Actiflo inlet | 23500 | No | Escalation | 0 | 2350 | 25850 | 2036 | 0 | 45328.1315 | 0 | 4120.7392 | 0 | 6 | 6 | 2035 | 2035
20 | Repair & Replace | Actiflo™ | Replace the five solids pumps (installed and standby) on the existing Actiflo basins | 640000 | No | Escalation | 0 | 64000 | 704000 | 2036 | 0 | 1234468.2614 | 0 | 112224.3874 | 0 | 6 | 6 | 2035 | 2035
21 | 30 MGD Expansion | Actiflo™ | Replace the two installed flash mix pumps | 378229 | Yes | Escalation | 56734.35 | 37822.9 | 472786.25 | 2034 | 0 | 781443.6339 | 93773.2361 | 62515.4907 | 12 | 24 | 6 | 2030 | 2031
22 | Repair & Replace | Actiflo™ | Replace the six mixers installed in the two existing Actiflo Basins | 302400 | No | Escalation | 0 | 30240 | 332640 | 2036 | 0 | 583286.2535 | 0 | 53026.023 | 0 | 6 | 6 | 2035 | 2035
23 | Repair & Replace | Actiflo™ | Replace the four hydrocyclones installed in the two existing Actiflo Basins | 369000 | No | Escalation | 0 | 36900 | 405900 | 2036 | 0 | 711748.1069 | 0 | 64704.3734 | 0 | 6 | 6 | 2035 | 2035
24 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Existing chemical lines are inaccessible south of the utilidor and cannot be inspected or replaced. Abandon existing lines in-place, extend utilidor to the southern end of the plant, and install chemical lines in the extended utilidor. | 566752 | Yes | Escalation | 85012.8 | 56675.2 | 708440 | 2022 | 0 | 821276.1252 | 98553.135 | 65702.09 | 12 | 18 | 6 | 2019 | 2020
25 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Replace existing 6,000 gallon LOX storage tank with larger tank (12,000 to 15,000 gallons) to ensure sufficient storage with 20 MGD plant capacity. Recommend purchasing LOX tank (rather than leasing from vendor) so LOX can be purchased from different vendors. | 262500 | Yes | Escalation | 39375 | 26250 | 328125 | 2034 | 0 | 542340.6293 | 65080.8755 | 43387.2503 | 12 | 24 | 6 | 2030 | 2031
26 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | On existing hypochlorite system, add ventilation line that returns to tank to prevent offgassing to atmosphere. | 7144 | Yes | Escalation | 1071.6 | 714.4 | 8930 | 2021 | 0 | 10050.7937 | 1206.0952 | 804.0635 | 12 | 18 | 6 | 2018 | 2019
27 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | On all existing chemical systems, add wye or basket strainers to all pump suction lines | 10978 | Yes | Escalation | 1646.7 | 1097.8 | 13722.5 | 2021 | 0 | 15444.7946 | 1853.3754 | 1235.5836 | 12 | 18 | 6 | 2018 | 2019
28 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Install a second dry polymer feeder to provide redundancy to plant chemical operations | 240000 | Yes | Escalation | 36000 | 24000 | 300000 | 2034 | 0 | 495854.2897 | 59502.5148 | 39668.3432 | 12 | 24 | 6 | 2030 | 2031
29 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Install a third 400 PPD ozone generator to support plant capacity expansion | 1193917 | Yes | Escalation | 179087.55 | 119391.7 | 1492396.25 | 2034 | 0 | 2466703.6082 | 296004.433 | 197336.2887 | 12 | 24 | 6 | 2030 | 2031
30 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Convert hypochlorite system from liquid chemical storage to dry sodium hypochlorite process system for increased storage capacity and plant resiliency. | 637883 | Yes | Escalation | 95682.45 | 63788.3 | 797353.75 | 2034 | 0 | 1317904.2578 | 158148.5109 | 105432.3406 | 12 | 24 | 6 | 2030 | 2031
31 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Modify existing Chemical Storage Room to increase usable space for existing chemical systems. Recommendations include installation of roll-up door, removal of aqueous ammonia system, modifications necessary to expand hypochlorite system, and modifications to chemical containment to allow additional tanks. | 160350 | Yes | Escalation | 24052.5 | 16035 | 200437.5 | 2034 | 0 | 331292.6473 | 39755.1177 | 26503.4118 | 12 | 24 | 6 | 2030 | 2031
32 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | The chemical pipes that run through the center of the Chemical Storage Room are not seismically braced. Ozone and LOX piping in the Ozone Generation Room are not sesimically braced. Provide seismic bracing for these lines. (LS19, LS20) | 36926 | No | Escalation | 0 | 3692.6 | 40618.6 | 2022 | 0 | 47088.0899 | 0 | 4280.7354 | 6 | 6 | 3 | 2020 | 2021
33 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Color-coded NFPA placards have faded. Replace all faded NFPA placards (LS2) | 9205 | No | Escalation | 0 | 920.5 | 10125.5 | 2022 | 0 | 11738.2296 | 0 | 1067.1118 | 6 | 6 | 3 | 2020 | 2021
34 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Chemical Storage and Ozone Generation Rooms are Group H occupancy or rated electrical service of 1200 A. Install panic hardware on three exit doors in the chemical storage and ozone generation building. (LS4; LS5) | 10517 | No | Escalation | 0 | 1051.7 | 11568.7 | 2022 | 0 | 13411.294 | 0 | 1219.2085 | 6 | 6 | 3 | 2020 | 2021
35 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Change swing direction on exit door between the ozone generation and administration building (LS5) | 5067 | No | Escalation | 0 | 506.7 | 5573.7 | 2022 | 0 | 6461.4459 | 0 | 587.4042 | 6 | 6 | 3 | 2020 | 2021
36 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Chemical lines pass above egress routes. Add containment pans to chemical conveyance lines that are located above doorways in the chemical storage and ozone generation building (LS6) | 11985 | No | Escalation | 0 | 1198.5 | 13183.5 | 2022 | 0 | 15283.2898 | 0 | 1389.39 | 6 | 6 | 3 | 2020 | 2021
37 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Install emergency shut-off at the two other exits in the Ozone Generation Room exits (LS15) | 11664 | No | Escalation | 0 | 1166.4 | 12830.4 | 2022 | 0 | 14873.9501 | 0 | 1352.1773 | 6 | 6 | 3 | 2020 | 2021
38 | Repair & Replace | Chemical Storage/ Ozone Generation | Upgrade vendor PLC components in the existing dry polymer blending unit | 22060 | No | Escalation | 0 | 2206 | 24266 | 2022 | 0 | 28130.9447 | 0 | 2557.3586 | 0 | 6 | 6 | 2021 | 2021
40 | Repair & Replace | Chemical Storage/ Ozone Generation | Replate two existing 300 PPD ozone generators with 400 PPD units | 1752000 | No | Escalation | 0 | 175200 | 1927200 | 2022 | 0 | 2234152.996 | 0 | 203104.8178 | 0 | 6 | 6 | 2021 | 2021
41 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Replace existing 4,400 gallon XLPE sodium hypochlorite tank with a 3,900 gallon tank | 52500 | Yes | Escalation | 7875 | 5250 | 65625 | 2021 | 0 | 73861.5157 | 8863.3819 | 5908.9213 | 12 | 18 | 6 | 2018 | 2019
42 | Repair & Replace | Chemical Storage/ Ozone Generation | Inspect existing alum tank and repair as needed | 52500 | No | Escalation | 0 | 5250 | 57750 | 2022 | 0 | 66948.0778 | 0 | 6086.1889 | 0 | 6 | 6 | 2021 | 2021
43 | Repair & Replace | Chemical Storage/ Ozone Generation | Inspect existing caustic soda tank and repair as needed | 52500 | No | Escalation | 0 | 5250 | 57750 | 2022 | 0 | 66948.0778 | 0 | 6086.1889 | 0 | 6 | 6 | 2021 | 2021
44 | Repair & Replace | Chemical Storage/ Ozone Generation | Replace the LOX evaporator equipment | 112500 | No | Escalation | 0 | 11250 | 123750 | 2036 | 0 | 216996.3741 | 0 | 19726.9431 | 0 | 6 | 6 | 2035 | 2035
46 | 20 MGD Expansion | Electrical | Install 15 KV/1,200 A metering/distribution switchgear | 4147606 | Yes | Escalation | 622140.9 | 414760.6 | 5184507.5 | 2021 | 0 | 5835208.8668 | 700225.064 | 466816.7093 | 12 | 18 | 6 | 2018 | 2019
47 | 20 MGD Expansion | Electrical | Install new 5,000 KVA transformer to control power distribution to raw and finished water pumps | 180000 | Yes | Escalation | 27000 | 18000 | 225000 | 2021 | 0 | 253239.4822 | 30388.7379 | 20259.1586 | 12 | 18 | 6 | 2018 | 2019
48 | 20 MGD Expansion | Electrical | Rewire existing electrical system to install new switchgear and transformer, connect all raw and finished water pumps to new transformer, connect new 2 MW emergency generator to switchgear, and upgrade existing electrical connections as needed to support new layout. | 285988 | Yes | Escalation | 42898.2 | 28598.8 | 357485 | 2021 | 0 | 402352.5169 | 48282.302 | 32188.2014 | 12 | 18 | 6 | 2018 | 2019
49 | 20 MGD Expansion | Electrical | Replace existing 1 MW generator with 2 MW generator | 4014088 | Yes | Escalation | 602113.2 | 401408.8 | 5017610 | 2021 | 0 | 5647364.2601 | 677683.7112 | 451789.1408 | 12 | 18 | 6 | 2018 | 2019
60 | 30 MGD Expansion | Filters | Construct two new media filters to support plant expansion to 30 MGD | 4185194 | Yes | Escalation | 627779.1 | 418519.4 | 5231492.5 | 2034 | 0 | 8646859.9919 | 1037623.199 | 691748.7993 | 12 | 24 | 6 | 2030 | 2031
61 | Life-Safety Repairs | Filters | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | Escalation | 0 | 642.7 | 7069.7 | 2022 | 0 | 8195.7199 | 0 | 745.0654 | 6 | 6 | 3 | 2020 | 2021
62 | Life-Safety Repairs | Filters | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 34854 | No | Escalation | 0 | 3485.4 | 38339.4 | 2022 | 0 | 44445.8724 | 0 | 4040.5339 | 6 | 6 | 3 | 2020 | 2021
63 | Life-Safety Repairs | Filters | The west guardrail on top of the the Filter ladder pit does not have continuous kickplates. Install new kickplates as required. (LS8) | 2305 | No | Escalation | 0 | 230.5 | 2535.5 | 2022 | 0 | 2939.3394 | 0 | 267.2127 | 6 | 6 | 3 | 2020 | 2021
64 | Life-Safety Repairs | Filters | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 4851 | No | Escalation | 0 | 485.1 | 5336.1 | 2022 | 0 | 6186.0024 | 0 | 562.3639 | 6 | 6 | 3 | 2020 | 2021
65 | Life-Safety Repairs | Filters | Add a fire-rated door at the bottom of the filter gallery stairs and add signage to existing ladder pit door to clarify that it is not an exit. (LS12) | 3505 | No | Escalation | 0 | 350.5 | 3855.5 | 2022 | 0 | 4469.5812 | 0 | 406.3256 | 6 | 6 | 3 | 2020 | 2021
66 | Life-Safety Repairs | Filters | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required in the air scour blower room. (LS7) | 43493 | No | Escalation | 0 | 4349.3 | 47842.3 | 2022 | 0 | 55462.338 | 0 | 5042.0307 | 6 | 6 | 3 | 2020 | 2021
68 | Repair & Replace | Filters | Replace existing air scour blowers and motors on existing media filtration system | 351000 | No | Escalation | 0 | 35100 | 386100 | 2022 | 0 | 447595.7201 | 0 | 40690.52 | 0 | 6 | 6 | 2021 | 2021
69 | 20 MGD Expansion | Filters | Upgrade electrical wiring as necessary to support plant-wide electrical upgrades | 238323 | Yes | Escalation | 35748.45 | 23832.3 | 297903.75 | 2021 | 0 | 335293.2952 | 40235.1954 | 26823.4636 | 12 | 18 | 6 | 2018 | 2019
73 | Repair & Replace | Filters | Replace aging MCC in existing filter gallery | 70000 | No | Escalation | 0 | 7000 | 77000 | 2036 | 0 | 135019.9661 | 0 | 12274.5424 | 0 | 6 | 6 | 2035 | 2035
74 | Repair & Replace | Filters | Replace air scour blowers and motors on existing media filtration system | 402000 | No | Escalation | 0 | 40200 | 442200 | 2036 | 0 | 775400.3767 | 0 | 70490.9433 | 0 | 6 | 6 | 2035 | 2035
75 | 20 MGD Expansion | Finished Water Pump Station | Replace existing 4 MGD pump with 7.5 MGD pump to ensure plant meets 20 MGD firm capacity. Alternately, install a fifth pump that is at least 5 MGD. | 1212081 | Yes | Escalation | 181812.15 | 121208.1 | 1515101.25 | 2021 | 0 | 1705259.8049 | 204631.1766 | 136420.7844 | 12 | 18 | 6 | 2018 | 2019
76 | 30 MGD Expansion | Finished Water Pump Station | Upgrade three existing 7.5 MGD finished water pumps with three 12 MGD pumps | 4896098 | Yes | Escalation | 734414.7 | 489609.8 | 6120122.5 | 2034 | 0 | 10115629.9833 | 1213875.598 | 809250.3987 | 12 | 24 | 6 | 2030 | 2031
77 | 30 MGD Expansion | Finished Water Pump Station | Install a fifth finished water pump as part of the 30 MGD upgrade. Recommend 7.5 MGD pump (only valid if not installed during 20 MGD expansion) | 1185023 | Yes | Escalation | 177753.45 | 118502.3 | 1481278.75 | 2034 | 0 | 2448328.0747 | 293799.369 | 195866.246 | 12 | 24 | 6 | 2030 | 2031
79 | Life-Safety Repairs | Finished Water Pump Station | The cable trays lack longitudinal bracing. Add bracing to existing cable trays. (LS18) | 14553 | No | Escalation | 0 | 1455.3 | 16008.3 | 2022 | 0 | 18558.0072 | 0 | 1687.0916 | 6 | 6 | 3 | 2020 | 2021
80 | Life-Safety Repairs | Finished Water Pump Station | The rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | Escalation | 0 | 701.1 | 7712.1 | 2022 | 0 | 8940.4376 | 0 | 812.7671 | 6 | 6 | 3 | 2020 | 2021
81 | Life-Safety Repairs | Finished Water Pump Station | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required in the finished water pump station. (LS7) | 81982 | No | Escalation | 0 | 8198.2 | 90180.2 | 2022 | 0 | 104543.5679 | 0 | 9503.9607 | 6 | 6 | 3 | 2020 | 2021
82 | Life-Safety Repairs | Finished Water Pump Station | Switchgear Room has rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | Escalation | 0 | 701.1 | 7712.1 | 2022 | 0 | 8940.4376 | 0 | 812.7671 | 6 | 6 | 3 | 2020 | 2021
83 | Repair & Replace | Finished Water Pump Station | Replace VFDs on three Finished Water Pumps | 596336 | No | Escalation | 0 | 59633.6 | 655969.6 | 2019 | 0 | 695918.1486 | 0 | 63265.2862 | 0 | 6 | 6 | 2018 | 2018
84 | Repair & Replace | Finished Water Pump Station | Replace existing soft-start controller on High Service Pump 3 | 84000 | No | Escalation | 0 | 8400 | 92400 | 2027 | 0 | 124177.8735 | 0 | 11288.8976 | 0 | 6 | 6 | 2026 | 2026
85 | Repair & Replace | Finished Water Pump Station | Replace two existing backwash supply pumps in the Wastewater Equalization Basin | 1980000 | No | Escalation | 0 | 198000 | 2178000 | 2032 | 0 | 3393253.0334 | 0 | 308477.5485 | 0 | 6 | 6 | 2031 | 2031
86 | Seismic Retrofits | Finished Water Pump Station | The roof joist wall anchorage along the east and west walls of the High Service PS have a DCR of 1.55. Add new wall anchorage along the east and west walls between the existing roof joists. (S3) | 144364 | Yes | Escalation | 21654.6 | 14436.4 | 180455 | 2022 | 0 | 209196.8031 | 25103.6164 | 16735.7442 | 6 | 6 | 3 | 2020 | 2021
87 | Seismic Retrofits | Finished Water Pump Station | The roof diaphragm shear at the High Service PS has a DCR of 1.82 to 2.25. Replace existing deficient deck sections with 16 GA corrugated steel decking. (S4) | 125618 | Yes | Escalation | 18842.7 | 12561.8 | 157022.5 | 2022 | 0 | 182032.1133 | 21843.8536 | 14562.5691 | 6 | 6 | 3 | 2020 | 2021
88 | Seismic Retrofits | Finished Water Pump Station | Tension capacity of the diaphragm chords at the High Service PS has a DCR of 1.20 at connections at the east windows. Strengthen chord splices as required. (S5) | 12159 | Yes | Escalation | 1823.85 | 1215.9 | 15198.75 | 2022 | 0 | 17619.5168 | 2114.342 | 1409.5613 | 6 | 6 | 3 | 2020 | 2021
89 | Seismic Retrofits | Finished Water Pump Station | Roof deck shear transfer to interior wall ledger bolts at the High Service PS have DCR’s of 3.20 to 3.90. Add new top plate over exterior shear wall and install epoxied anchors. (S6) | 87647 | Yes | Escalation | 13147.05 | 8764.7 | 109558.75 | 2022 | 0 | 127008.6185 | 15241.0342 | 10160.6895 | 6 | 6 | 3 | 2020 | 2021
92 | Repair & Replace | Miscellaneous | Replace the existing safety and warning signs throughout the site | 15000 | No | Escalation | 0 | 1500 | 16500 | 2022 | 0 | 19128.0222 | 0 | 1738.9111 | 0 | 6 | 6 | 2021 | 2021
93 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2020 | 0 | 8413.9979 | 0 | 764.9089 | 0 | 6 | 6 | 2019 | 2019
94 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2020 | 0 | 5258.7487 | 0 | 478.0681 | 0 | 6 | 6 | 2019 | 2019
95 | Repair & Replace | Miscellaneous | Upgrade site security monitoring system camera and computer | 23500 | No | Escalation | 0 | 2350 | 25850 | 2020 | 0 | 28246.993 | 0 | 2567.9084 | 0 | 6 | 6 | 2019 | 2019
96 | Repair & Replace | Miscellaneous | Replace sitewide fire extinguishers | 15000 | No | Escalation | 0 | 1500 | 16500 | 2022 | 0 | 19128.0222 | 0 | 1738.9111 | 0 | 6 | 6 | 2021 | 2021
97 | Repair & Replace | Miscellaneous | Replace the two existing irrigation waste pumps (T-30P01/2) | 340000 | No | Escalation | 0 | 34000 | 374000 | 2022 | 0 | 433568.5038 | 0 | 39415.3185 | 0 | 6 | 6 | 2021 | 2021
98 | Repair & Replace | Miscellaneous | Replace the two existing water feature pumps (T-30P01/2) | 340000 | No | Escalation | 0 | 34000 | 374000 | 2027 | 0 | 502624.7259 | 0 | 45693.1569 | 0 | 6 | 6 | 2026 | 2026
99 | 20 MGD Expansion | Miscellaneous | Replace two existing rooftop HVAC units in the Administration Building (Conference Room and Control Room) and repair ventilation in Laboratory (T-18HVAC01 through 3) | 184250 | Yes | Escalation | 27637.5 | 18425 | 230312.5 | 2019 | 0 | 244338.5312 | 29320.6237 | 19547.0825 | 12 | 18 | 6 | 2016 | 2017
100 | 20 MGD Expansion | Ozonation | Replace the diffusers in the two existing ozone basins to support 30 MGD capacity expansion | 73000 | Yes | Escalation | 10950 | 7300 | 91250 | 2021 | 0 | 102702.6789 | 12324.3215 | 8216.2143 | 12 | 18 | 6 | 2018 | 2019
101 | 30 MGD Expansion | Ozonation | Construct a third ozone basin and gallery to support 30 MGD expansion | 3420955 | Yes | Escalation | 513143.25 | 342095.5 | 4276193.75 | 2034 | 0 | 7067896.7148 | 848147.6058 | 565431.7372 | 12 | 24 | 6 | 2030 | 2031
102 | Life-Safety Repairs | Ozonation | The ozone destruct pipe on the top side is not seismically braced or marked. Add chemical service label and provide seismic bracing down to the concrete deck. (LS17) | 11809 | No | Escalation | 0 | 1180.9 | 12989.9 | 2022 | 0 | 15058.8543 | 0 | 1368.9868 | 6 | 6 | 3 | 2020 | 2021
103 | Life-Safety Repairs | Ozonation | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | Escalation | 0 | 642.7 | 7069.7 | 2022 | 0 | 8195.7199 | 0 | 745.0654 | 6 | 6 | 3 | 2020 | 2021
104 | Life-Safety Repairs | Ozonation | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 44468 | No | Escalation | 0 | 4446.8 | 48914.8 | 2022 | 0 | 56705.6595 | 0 | 5155.06 | 6 | 6 | 3 | 2020 | 2021
105 | Life-Safety Repairs | Ozonation | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 2425 | No | Escalation | 0 | 242.5 | 2667.5 | 2022 | 0 | 3092.3636 | 0 | 281.124 | 6 | 6 | 3 | 2020 | 2021
106 | Life-Safety Repairs | Ozonation | The south stairwell does not have any ventilation system serving it directly. Investigate and repair as required. (LS11) | 10499 | No | Escalation | 0 | 1049.9 | 11548.9 | 2022 | 0 | 13388.3404 | 0 | 1217.1219 | 6 | 6 | 3 | 2020 | 2021
107 | 20 MGD Expansion | Raw Water Pump Station | Replace existing 4 MGD pump with 7.5 MGD pump to ensure plant meets 20 MGD firm capacity with three dedicated pumps | 665000 | Yes | Escalation | 99750 | 66500 | 831250 | 2021 | 0 | 935579.1983 | 112269.5038 | 74846.3359 | 12 | 18 | 6 | 2018 | 2019
108 | 30 MGD Expansion | Raw Water Pump Station | Replace two existing 7.5 MGD pumps with 15 MGD pumps | 1772847 | Yes | Escalation | 265927.05 | 177284.7 | 2216058.75 | 2034 | 0 | 3662807.4579 | 439536.8949 | 293024.5966 | 12 | 24 | 6 | 2030 | 2031
109 | Repair & Replace | Raw Water Pump Station | Replace existing raw water sump pump | 100000 | No | Escalation | 0 | 10000 | 110000 | 2020 | 0 | 120199.97 | 0 | 10927.27 | 0 | 6 | 6 | 2019 | 2019
110 | Repair & Replace | Raw Water Pump Station | Replace osbsolete Robocon VFDs on three Raw Water Pumps | 97375 | No | Escalation | 0 | 9737.5 | 107112.5 | 2019 | 0 | 113635.6513 | 0 | 10330.5137 | 0 | 6 | 6 | 2018 | 2018
111 | Repair & Replace | Raw Water Pump Station | Replace two existing Air Burst Compressors | 395000 | No | Escalation | 0 | 39500 | 434500 | 2027 | 0 | 583931.6668 | 0 | 53084.697 | 0 | 6 | 6 | 2026 | 2026
112 | Repair & Replace | Raw Water Pump Station | Replace existing air burst control panel PLC and local control panel | 42375 | No | Escalation | 0 | 4237.5 | 46612.5 | 2027 | 0 | 62643.3022 | 0 | 5694.8457 | 0 | 6 | 6 | 2026 | 2026
113 | Repair & Replace | Raw Water Pump Station | Replace the existing constant-speed 7.5 MGD pump with a VFD-controlled pump | 682500 | No | Escalation | 0 | 68250 | 750750 | 2036 | 0 | 1316444.6693 | 0 | 119676.7881 | 0 | 6 | 6 | 2035 | 2035
114 | 20 MGD Expansion | Sitewide | Sitewide lighting upgrade to support continued nighttime operations. For purpose of cost estimate, assuming that sitewide external lighting is replaced with high efficiency LED system. | 156532 | Yes | Escalation | 23479.8 | 15653.2 | 195665 | 2021 | 0 | 220222.6813 | 26426.7218 | 17617.8145 | 12 | 18 | 6 | 2018 | 2019
115 | Life-Safety Repairs | Sitewide | The space heaters throughout the plant are laterally braced above their center of gravity. The space heaters at the Switchgear Room are not braced. Provide additional seismic bracing to approximately eight locations. (LS16) | 11827 | No | Escalation | 0 | 1182.7 | 13009.7 | 2022 | 0 | 15081.8079 | 0 | 1371.0734 | 6 | 6 | 3 | 2020 | 2021
116 | Life-Safety Repairs | Sitewide | Tread plate hatches do not have provisions for installing temporary fall protection barriers. Install sleeves or other hardware for temporary fall protection. (LS1) | 42284 | No | Escalation | 0 | 4228.4 | 46512.4 | 2022 | 0 | 53920.6195 | 0 | 4901.8745 | 6 | 6 | 3 | 2020 | 2021
117 | Repair & Replace | Sitewide | Replace obsolete ABB magnetic flow meters installed throughout the WRWTP and at Wilsonville Road | 662400 | No | Escalation | 0 | 66240 | 728640 | 2019 | 0 | 773014.176 | 0 | 70274.016 | 0 | 6 | 6 | 2018 | 2018
118 | 30 MGD Expansion | Solids - Dewatering | Install a third 60 GPM centrifuge and solids transfer pump to support the 30 MGD plant expansion | 1665316 | Yes | Escalation | 249797.4 | 166531.6 | 2081645 | 2034 | 0 | 3440642.0095 | 412877.0411 | 275251.3608 | 12 | 24 | 6 | 2030 | 2031
119 | Life-Safety Repairs | Solids - Dewatering | The Solids Handling Building roof does not appear to have an overflow scupper. Provide an overflow scupper with downspout. (LS14) | 8855 | No | Escalation | 0 | 885.5 | 9740.5 | 2022 | 0 | 11291.9091 | 0 | 1026.5372 | 6 | 6 | 3 | 2020 | 2021
120 | Repair & Replace | Solids - Dewatering | Replace the existing dewatered sludge screw conveyor in the Solids Handling Building | 87000 | No | Escalation | 0 | 8700 | 95700 | 2022 | 0 | 110942.5289 | 0 | 10085.6844 | 0 | 6 | 6 | 2021 | 2021
121 | Repair & Replace | Solids - Dewatering | Replace two existing 60 GPM centrifuges and transfer pumps | 3500000 | No | Escalation | 0 | 350000 | 3850000 | 2027 | 0 | 5174078.0605 | 0 | 470370.7328 | 0 | 6 | 6 | 2026 | 2026
122 | Repair & Replace | Solids - Dewatering | Replace existing PLC and local control panel for two dewatering centrifuges | 84000 | No | Escalation | 0 | 8400 | 92400 | 2027 | 0 | 124177.8735 | 0 | 11288.8976 | 0 | 6 | 6 | 2026 | 2026
123 | Repair & Replace | Solids - Dewatering | Replace two existing 60 GPM solids transfer pumps | 316059 | No | Escalation | 0 | 31605.9 | 347664.9 | 2036 | 0 | 609632.5066 | 0 | 55421.137 | 0 | 6 | 6 | 2035 | 2035
124 | Seismic Retrofits | Solids - Dewatering | The Solids Handling Building has no lateral load resisting system in the transverse direction at the lower level. Provide structural bracing in the east-west direction by installation of shear wall extensions or exterior steel bracing. (S7) | 47722 | Yes | Escalation | 7158.3 | 4772.2 | 59652.5 | 2022 | 0 | 69153.5967 | 8298.4316 | 5532.2877 | 6 | 6 | 3 | 2020 | 2021
125 | Seismic Retrofits | Solids - Dewatering | The roof joist wall anchorage along the east and west walls of the Solids Handling Building have a DCR of 1.17. Add new wall anchorage along the east and west walls between the existing roof joists. (S8) | 62761 | Yes | Escalation | 9414.15 | 6276.1 | 78451.25 | 2022 | 0 | 90946.5002 | 10913.58 | 7275.72 | 6 | 6 | 3 | 2020 | 2021
126 | Seismic Retrofits | Solids - Dewatering | The foundation elements at the Solids Handling Building do not have adequate ties. The floor slab is not doweled into the walls or the footings. Tie the existing slab to the walls with stainless steel angles and epoxy anchors. (S9) | 24672 | Yes | Escalation | 3700.8 | 2467.2 | 30840 | 2022 | 0 | 35752.0125 | 4290.2415 | 2860.161 | 6 | 6 | 3 | 2020 | 2021
127 | 20 MGD Expansion | Solids - Gravity Thickener | To increase solids mixing redundancy, recommend purchasing and installing a second mixing pump to give 1+1 configuration | 104385 | Yes | Escalation | 15657.75 | 10438.5 | 130481.25 | 2021 | 0 | 146857.7964 | 17622.9356 | 11748.6237 | 12 | 18 | 6 | 2018 | 2019
128 | 30 MGD Expansion | Solids - Gravity Thickener | Construct a second 35-ft diameter gravity thickener to support the 30 MGD plant expansion and provide solids handling redundancy | 870475 | Yes | Escalation | 130571.25 | 87047.5 | 1088093.75 | 2034 | 0 | 1798453.1784 | 215814.3814 | 143876.2543 | 12 | 24 | 6 | 2030 | 2031
129 | Repair & Replace | Solids - Gravity Thickener | Replace two existing sludge mixing pumps (one installed, one shelf spare) | 260000 | No | Escalation | 0 | 26000 | 286000 | 2020 | 0 | 312519.922 | 0 | 28410.902 | 0 | 6 | 6 | 2019 | 2019
130 | Repair & Replace | Solids - Gravity Thickener | Replace the two existing sludge mixing pumps | 260000 | No | Escalation | 0 | 26000 | 286000 | 2032 | 0 | 445578.6811 | 0 | 40507.1528 | 0 | 6 | 6 | 2031 | 2031
131 | Repair & Replace | Solids - Gravity Thickener | Replace the existing gravity thickener drive | 114264 | No | Escalation | 0 | 11426.4 | 125690.4 | 2036 | 0 | 220398.8772 | 0 | 20036.2616 | 0 | 6 | 6 | 2035 | 2035
132 | 30 MGD Expansion | WWEQ Basin | Install fourth washwater recycle pump for additional redundancy at 30 MGD expansion | 281250 | Yes | Escalation | 42187.5 | 28125 | 351562.5 | 2034 | 0 | 581079.2457 | 69729.5095 | 46486.3397 | 12 | 24 | 6 | 2030 | 2031
133 | Life-Safety Repairs | WWEQ Basin | Verify how fall restraint is provided when using the ladder into the waste washwaster equalization basin and provide additional hardware as required. (LS13) | 7546 | No | Escalation | 0 | 754.6 | 8300.6 | 2022 | 0 | 9622.6704 | 0 | 874.7882 | 6 | 6 | 3 | 2020 | 2021
134 | Life-Safety Repairs | WWEQ Basin | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required at waste washwater equalization basin. (LS7) | 35168 | No | Escalation | 0 | 3516.8 | 38684.8 | 2022 | 0 | 44846.2857 | 0 | 4076.9351 | 6 | 6 | 3 | 2020 | 2021
135 | Repair & Replace | WWEQ Basin | Replace three existing filter waste washwater recycle pumps | 300000 | No | Escalation | 0 | 30000 | 330000 | 2020 | 0 | 360599.91 | 0 | 32781.81 | 0 | 6 | 6 | 2019 | 2019
136 | 20 MGD Expansion | WWEQ Basin | Modifications necessary to support chemical pipelines along western WWEQ Basin wall | 300000 | Yes | Escalation | 45000 | 30000 | 375000 | 2022 | 0 | 434727.7779 | 52167.3333 | 34778.2222 | 12 | 18 | 6 | 2019 | 2020
137 | Repair & Replace | WWEQ Basin | Replace three existing filter waste washwater recycle pumps | 43036 | No | Escalation | 0 | 4303.6 | 47339.6 | 2036 | 0 | 83010.2752 | 0 | 7546.3887 | 0 | 6 | 6 | 2035 | 2035
138 | Seismic Retrofits | WWEQ Basin | Waste Washwater EQ Basin North & South Walls: Horizontal reinforcing steel at east corners (#8 @ 12” OC) have a DCR of 1.53 for soil seismic loads. Recommend adding additional reinforced shotcrete to wall or adding three concete/steel braces across the basin. (S1) | 219386 | Yes | Escalation | 32907.9 | 21938.6 | 274232.5 | 2022 | 0 | 317910.6276 | 38149.2753 | 25432.8502 | 6 | 6 | 3 | 2020 | 2021
139 | Seismic Retrofits | WWEQ Basin | Waste Washwater EQ Basin North & South Walls: Wall shear at the concrete beam has a DCR of 1.67 for soil seismic loads. Recommend addition of reinforced shotcrete to wall or addition of concrete/steel braces across the basin. (S2) | 197164 | Yes | Escalation | 29574.6 | 19716.4 | 246455 | 2022 | 0 | 285708.892 | 34285.067 | 22856.7114 | 6 | 6 | 3 | 2020 | 2021
140 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Replace 6,000-gallon rented LOX tank with larger tank | 88917 | Yes | Escalation | 13337.55 | 8891.7 | 111146.25 | 2021 | 0 | 125096.0836 | 15011.53 | 10007.6867 | 12 | 18 | 6 | 2018 | 2019
141 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2021 | 0 | 8666.4178 | 0 | 787.8562 | 0 | 6 | 6 | 2020 | 2020
142 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2021 | 0 | 5416.5111 | 0 | 492.4101 | 0 | 6 | 6 | 2020 | 2020
143 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2022 | 0 | 8926.4104 | 0 | 811.4919 | 0 | 6 | 6 | 2021 | 2021
144 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2022 | 0 | 5579.0065 | 0 | 507.1824 | 0 | 6 | 6 | 2021 | 2021
145 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2023 | 0 | 9194.2027 | 0 | 835.8366 | 0 | 6 | 6 | 2022 | 2022
146 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2023 | 0 | 5746.3767 | 0 | 522.3979 | 0 | 6 | 6 | 2022 | 2022
147 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2024 | 0 | 9470.0288 | 0 | 860.9117 | 0 | 6 | 6 | 2023 | 2023
148 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2024 | 0 | 5918.768 | 0 | 538.0698 | 0 | 6 | 6 | 2023 | 2023
149 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2025 | 0 | 9754.1296 | 0 | 886.7391 | 0 | 6 | 6 | 2024 | 2024
150 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2025 | 0 | 6096.331 | 0 | 554.2119 | 0 | 6 | 6 | 2024 | 2024
151 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2026 | 0 | 10046.7535 | 0 | 913.3412 | 0 | 6 | 6 | 2025 | 2025
152 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2026 | 0 | 6279.2209 | 0 | 570.8383 | 0 | 6 | 6 | 2025 | 2025
153 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2027 | 0 | 10348.1561 | 0 | 940.7415 | 0 | 6 | 6 | 2026 | 2026
154 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2027 | 0 | 6467.5976 | 0 | 587.9634 | 0 | 6 | 6 | 2026 | 2026
155 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2028 | 0 | 10658.6008 | 0 | 968.9637 | 0 | 6 | 6 | 2027 | 2027
156 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2028 | 0 | 6661.6255 | 0 | 605.6023 | 0 | 6 | 6 | 2027 | 2027
157 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2029 | 0 | 10978.3588 | 0 | 998.0326 | 0 | 6 | 6 | 2028 | 2028
158 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2029 | 0 | 6861.4743 | 0 | 623.7704 | 0 | 6 | 6 | 2028 | 2028
159 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2030 | 0 | 11307.7096 | 0 | 1027.9736 | 0 | 6 | 6 | 2029 | 2029
160 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2030 | 0 | 7067.3185 | 0 | 642.4835 | 0 | 6 | 6 | 2029 | 2029
161 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2031 | 0 | 11646.9409 | 0 | 1058.8128 | 0 | 6 | 6 | 2030 | 2030
162 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2031 | 0 | 7279.3381 | 0 | 661.758 | 0 | 6 | 6 | 2030 | 2030
163 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2032 | 0 | 11996.3491 | 0 | 1090.5772 | 0 | 6 | 6 | 2031 | 2031
164 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2032 | 0 | 7497.7182 | 0 | 681.6107 | 0 | 6 | 6 | 2031 | 2031
165 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2033 | 0 | 12356.2396 | 0 | 1123.2945 | 0 | 6 | 6 | 2032 | 2032
166 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2033 | 0 | 7722.6497 | 0 | 702.0591 | 0 | 6 | 6 | 2032 | 2032
167 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2034 | 0 | 12726.9268 | 0 | 1156.9933 | 0 | 6 | 6 | 2033 | 2033
168 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2034 | 0 | 7954.3292 | 0 | 723.1208 | 0 | 6 | 6 | 2033 | 2033
169 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2035 | 0 | 13108.7346 | 0 | 1191.7031 | 0 | 6 | 6 | 2034 | 2034
170 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2035 | 0 | 8192.9591 | 0 | 744.8145 | 0 | 6 | 6 | 2034 | 2034
171 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | Escalation | 0 | 700 | 7700 | 2036 | 0 | 13501.9966 | 0 | 1227.4542 | 0 | 6 | 6 | 2035 | 2035
172 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | Escalation | 0 | 437.5 | 4812.5 | 2036 | 0 | 8438.7479 | 0 | 767.1589 | 0 | 6 | 6 | 2035 | 2035
173 | 30 MGD Expansion | Finished Water Pump Station | Temporary pump station to supply 15 MGD from the WWSP Treatment Plant to the WRWTP distribution system in the event of a service distruption. | 4896098 | Yes | Escalation | 734414.7 | 489609.8 | 6120122.5 | 2034 | 0 | 10115629.9833 | 1213875.598 | 809250.3987 | 12 | 24 | 6 | 2030 | 2031
174 | 20 MGD Expansion | Finished Water Pump Station | Conduct tracer study in support of receiving OHA ozonation waiver | 50000 | Yes | Escalation | 7500 | 5000 | 62500 | 2021 | 0 | 70344.3006 | 8441.3161 | 5627.544 | 12 | 18 | 6 | 2018 | 2019
|  |  | TOTAL COSTS | 56193027 |  |  |  |  | 67738302.15
Notes:
(1) |  | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
Note on A7: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B7: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C7: Meghann Chell: Identifies WTP plant system associated with task.
Note on D7: Meghann Chell: Description of task scope used to develop estimate.
Note on E7: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook.
Note on F7: Meghann Chell: Yes - Design and Admin Contingency added No - Only Admin Contingency added
Note on G7: Natalie Reilly: If "Escalation", project costs are calculated using escalation rate selected on this sheet. If "Revised ENR", project costs are calculated using ratio of "ENR @ Date" and "ENR @ Revised Estimate Date" and escalation rate beyond "Revised Estimate Date". Editable in CIP Summary sheet
Note on H7: Meghann Chell: Calculated design cost based on project construction cost and design escalation rate. Value is $0 if Design Project field = No.
Note on I7: Meghann Chell: Calculated adminstrative cost based on project construction cost and adminstration escalation rate.
Note on J7: Meghann Chell: Sum of Construction, Design, and Adminstrative Costs
Note on K7: Meghann Chell: Estimated year that project comes online. R&R Tasks are editable.
Note on L7: Meghann Chell: ENR value at project completion year. User entered value.
Note on M7: Meghann Chell: Future value of project based on assumed escalation rate.
Note on N7: Meghann Chell: Future design cost based on assumed escalation rate, ENR, or Revised ENR based on user selection
Note on O7: Meghann Chell: Future administrative cost based on assumed escalation rate, ENR, or Revised ENR based on user selection
Note on P7: Natalie Reilly: Assumed duration of project design. R&R Tasks can be edited.
Note on Q7: Natalie Reilly: Assumed duration of project construction. R&R Tasks can be edited.
Note on R7: Natalie Reilly: Assumed project float. R&R Tasks can be edited.
Note on S7: Natalie Reilly: Design start date caluclated based on Assumed Project Year, Design Duration, Construction Duration, and Float.
Note on T7: Natalie Reilly: Construction start date caluclated based on Assumed Project Year, Construction Duration, and Float
Note on C105: Meghann Chell: Change to plant-wide?

## P1
WILLAMETTE RIVER WATER TREATMENT PLANT
CAPITAL IMPROVEMENT PROGRAM UPDATE
PROJECT NO. 1
Project Title |  | 20 MGD Expansion
Project Category |  | Capacity Improvement
Project Description |  | The existing treatment processes will be uprated for the 20 mgd WRWTP expansion. For the primary treatment processes, the uprating will include the following: • Increasing the Actiflo® flow rate from 7.5 mgd per basin to 10 mgd per basin. • Increasing the ozonation basin flow rate from 7.5 mgd per basin to 10 mgd per basin. This will decrease the ozone contact time from 15 to 11 minutes, which still allows sufficient contact time for 1-log Cryptosporidium inactivation, provided increased levels of ozone can be dosed in the contactor. • Increasing the filtration rate to a nominal rate of 5.7 gpm/sf and a maximum rate of 7.5 gpm/sf when one filter is off-line, and to a nominal rate of 7.5 gpm/sf and a maximum rate of 10 gpm/sf when one basin is offline. This increased filtration rate will require approval from OHA prior to increasing plant capacity. To support OHA approval, a full scale pilot study should be conducted in which the filtration rate is gradually increased and water quality is closely monitored. • To meet the 2022 site capacity of nominally 20 mgd, the plant's electrical supply and distribution system will need significant upgrades. Preliminary engineering for the capacity expansion will require detailed analysis of electrical supply alternatives, including backup power requirements. Improving the "backbone" of electrical and standby power is recommended in parallel with the expansion project.
Project Summary Table
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Estimated Total Cost(1) | Future Value in Project Year - Escalation | Actual Construction Cost
1 | 20 MGD Expansion | Actiflo™ | Install second flash mix pump to give system installed redundancy (1+1) rather than shelf spare. | 169791 | Yes | 212238.75 | 238876.5829
2 | 20 MGD Expansion | Actiflo™ | Purchase additional shelf spare solid pump | 42275 | Yes | 52843.75 | 59476.1062
11 | 20 MGD Expansion | Actiflo™ | Replace and reinstall existing streaming current analyzer on Actiflo inlet so it can be used for chemical dosing | 70500 | Yes | 88125 | 96296.5669
24 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Existing chemical lines are inaccessible south of the utilidor and cannot be inspected or replaced. Abandon existing lines in-place, extend utilidor to the southern end of the plant, and install chemical lines in the extended utilidor. | 566752 | Yes | 708440 | 821276.1252
26 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | On existing hypochlorite system, add ventilation line that returns to tank to prevent offgassing to atmosphere. | 7144 | Yes | 8930 | 10050.7937
27 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | On all existing chemical systems, add wye or basket strainers to all pump suction lines | 10978 | Yes | 13722.5 | 15444.7946
41 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Replace existing 4,400 gallon XLPE sodium hypochlorite tank with a 3,900 gallon tank | 52500 | Yes | 65625 | 73861.5157
46 | 20 MGD Expansion | Electrical | Install 15 KV/1,200 A metering/distribution switchgear | 4147606 | Yes | 5184507.5 | 5835208.8668
47 | 20 MGD Expansion | Electrical | Install new 5,000 KVA transformer to control power distribution to raw and finished water pumps | 180000 | Yes | 225000 | 253239.4822
48 | 20 MGD Expansion | Electrical | Rewire existing electrical system to install new switchgear and transformer, connect all raw and finished water pumps to new transformer, connect new 2 MW emergency generator to switchgear, and upgrade existing electrical connections as needed to support new layout. | 285988 | Yes | 357485 | 402352.5169
49 | 20 MGD Expansion | Electrical | Replace existing 1 MW generator with 2 MW generator | 4014088 | Yes | 5017610 | 5647364.2601
69 | 20 MGD Expansion | Filters | Upgrade electrical wiring as necessary to support plant-wide electrical upgrades | 238323 | Yes | 297903.75 | 335293.2952
75 | 20 MGD Expansion | Finished Water Pump Station | Replace existing 4 MGD pump with 7.5 MGD pump to ensure plant meets 20 MGD firm capacity. Alternately, install a fifth pump that is at least 5 MGD. | 1212081 | Yes | 1515101.25 | 1705259.8049
99 | 20 MGD Expansion | Miscellaneous | Replace two existing rooftop HVAC units in the Administration Building (Conference Room and Control Room) and repair ventilation in Laboratory (T-18HVAC01 through 3) | 184250 | Yes | 230312.5 | 244338.5312
100 | 20 MGD Expansion | Ozonation | Replace the diffusers in the two existing ozone basins to support 30 MGD capacity expansion | 73000 | Yes | 91250 | 102702.6789
107 | 20 MGD Expansion | Raw Water Pump Station | Replace existing 4 MGD pump with 7.5 MGD pump to ensure plant meets 20 MGD firm capacity with three dedicated pumps | 665000 | Yes | 831250 | 935579.1983
114 | 20 MGD Expansion | Sitewide | Sitewide lighting upgrade to support continued nighttime operations. For purpose of cost estimate, assuming that sitewide external lighting is replaced with high efficiency LED system. | 156532 | Yes | 195665 | 220222.6813
127 | 20 MGD Expansion | Solids - Gravity Thickener | To increase solids mixing redundancy, recommend purchasing and installing a second mixing pump to give 1+1 configuration | 104385 | Yes | 130481.25 | 146857.7964
136 | 20 MGD Expansion | WWEQ Basin | Modifications necessary to support chemical pipelines along western WWEQ Basin wall | 300000 | Yes | 375000 | 434727.7779
140 | 20 MGD Expansion | Chemical Storage/ Ozone Generation | Replace 6,000-gallon rented LOX tank with larger tank | 88917 | Yes | 111146.25 | 125096.0836
174 | 20 MGD Expansion | Finished Water Pump Station | Conduct tracer study in support of receiving OHA ozonation waiver | 50000 | Yes | 62500 | 70344.3006
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
Note on A54: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B54: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C54: Meghann Chell: Identifies WTP plant system assocaited with task
Note on D54: Meghann Chell: Description of task scope used to develop estimate.
Note on E54: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook. Editable in CIP Full Sheet.
Note on F54: Meghann Chell: YES - Design and Admin Contingency added NO - Only Admin Contingency added Editable in CIP Full Sheet
Note on H54: Meghann Chell: Future value of project based on assumed escalation rate.
Note on I54: Natalie Reilly: Input actual construction cost

## P2
WILLAMETTE RIVER WATER TREATMENT PLANT
CAPITAL IMPROVEMENT PROGRAM UPDATE
PROJECT NO. 2
Project Title |  | Life-Safety Repairs
Project Category |  | Renewal and Replacement
Project Description |  | The preliminary life-safety analysis identified issues about building code compliance and structural improvements. This 2017 MPU recommends modifications to support worker safety after a catastrophic seismic event.
Project Summary Table
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Estimated Task Cost(1) | Future Value in Project Year - Escalation | Actual Construction Cost
4 | Life-Safety Repairs | Actiflo™ | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | 7069.7 | 8195.7199
5 | Life-Safety Repairs | Actiflo™ | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 36136 | No | 39749.6 | 46080.6807
6 | Life-Safety Repairs | Actiflo™ | The rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | 7712.1 | 8940.4376
7 | Life-Safety Repairs | Actiflo™ | The west guardrail on top of the Actiflo™ tanks does not have continuous kickplates. Install new kickplates as required. (LS8) | 2305 | No | 2535.5 | 2939.3394
8 | Life-Safety Repairs | Actiflo™ | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 2425 | No | 2667.5 | 3092.3636
9 | Life-Safety Repairs | Actiflo™ | The doors were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required at Actiflo™ building. (LS7) | 33171 | No | 36488.1 | 42299.7084
32 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | The chemical pipes that run through the center of the Chemical Storage Room are not seismically braced. Ozone and LOX piping in the Ozone Generation Room are not sesimically braced. Provide seismic bracing for these lines. (LS19, LS20) | 36926 | No | 40618.6 | 47088.0899
33 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Color-coded NFPA placards have faded. Replace all faded NFPA placards (LS2) | 9205 | No | 10125.5 | 11738.2296
34 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Chemical Storage and Ozone Generation Rooms are Group H occupancy or rated electrical service of 1200 A. Install panic hardware on three exit doors in the chemical storage and ozone generation building. (LS4; LS5) | 10517 | No | 11568.7 | 13411.294
35 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Change swing direction on exit door between the ozone generation and administration building (LS5) | 5067 | No | 5573.7 | 6461.4459
36 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Chemical lines pass above egress routes. Add containment pans to chemical conveyance lines that are located above doorways in the chemical storage and ozone generation building (LS6) | 11985 | No | 13183.5 | 15283.2898
37 | Life-Safety Repairs | Chemical Storage/ Ozone Generation | Install emergency shut-off at the two other exits in the Ozone Generation Room exits (LS15) | 11664 | No | 12830.4 | 14873.9501
61 | Life-Safety Repairs | Filters | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | 7069.7 | 8195.7199
62 | Life-Safety Repairs | Filters | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 34854 | No | 38339.4 | 44445.8724
63 | Life-Safety Repairs | Filters | The west guardrail on top of the the Filter ladder pit does not have continuous kickplates. Install new kickplates as required. (LS8) | 2305 | No | 2535.5 | 2939.3394
64 | Life-Safety Repairs | Filters | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 4851 | No | 5336.1 | 6186.0024
65 | Life-Safety Repairs | Filters | Add a fire-rated door at the bottom of the filter gallery stairs and add signage to existing ladder pit door to clarify that it is not an exit. (LS12) | 3505 | No | 3855.5 | 4469.5812
66 | Life-Safety Repairs | Filters | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required in the air scour blower room. (LS7) | 43493 | No | 47842.3 | 55462.338
79 | Life-Safety Repairs | Finished Water Pump Station | The cable trays lack longitudinal bracing. Add bracing to existing cable trays. (LS18) | 14553 | No | 16008.3 | 18558.0072
80 | Life-Safety Repairs | Finished Water Pump Station | The rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | 7712.1 | 8940.4376
81 | Life-Safety Repairs | Finished Water Pump Station | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required in the finished water pump station. (LS7) | 81982 | No | 90180.2 | 104543.5679
82 | Life-Safety Repairs | Finished Water Pump Station | Switchgear Room has rated electrical service is 1200 amps or greater requiring two exits with panic hardware. Install panic hardware on doors. (LS4) | 7011 | No | 7712.1 | 8940.4376
102 | Life-Safety Repairs | Ozonation | The ozone destruct pipe on the top side is not seismically braced or marked. Add chemical service label and provide seismic bracing down to the concrete deck. (LS17) | 11809 | No | 12989.9 | 15058.8543
103 | Life-Safety Repairs | Ozonation | Exterior stair guardrail height is less than 42” and has no dedicated handrail. Replace with current code-compliant installation. (LS3) | 6427 | No | 7069.7 | 8195.7199
104 | Life-Safety Repairs | Ozonation | Active leaks observed in the ozone gallery, creating a slip hazard. Pressure inject hydrophobic sealant into active leaks. Leaking joints may require negative side joint covers. (LS9) | 44468 | No | 48914.8 | 56705.6595
105 | Life-Safety Repairs | Ozonation | Electrical outlets on gallery walls are in a wet area. Replace with GFCI protected outlets. (LS10) | 2425 | No | 2667.5 | 3092.3636
106 | Life-Safety Repairs | Ozonation | The south stairwell does not have any ventilation system serving it directly. Investigate and repair as required. (LS11) | 10499 | No | 11548.9 | 13388.3404
115 | Life-Safety Repairs | Sitewide | The space heaters throughout the plant are laterally braced above their center of gravity. The space heaters at the Switchgear Room are not braced. Provide additional seismic bracing to approximately eight locations. (LS16) | 11827 | No | 13009.7 | 15081.8079
116 | Life-Safety Repairs | Sitewide | Tread plate hatches do not have provisions for installing temporary fall protection barriers. Install sleeves or other hardware for temporary fall protection. (LS1) | 42284 | No | 46512.4 | 53920.6195
119 | Life-Safety Repairs | Solids - Dewatering | The Solids Handling Building roof does not appear to have an overflow scupper. Provide an overflow scupper with downspout. (LS14) | 8855 | No | 9740.5 | 11291.9091
133 | Life-Safety Repairs | WWEQ Basin | Verify how fall restraint is provided when using the ladder into the waste washwaster equalization basin and provide additional hardware as required. (LS13) | 7546 | No | 8300.6 | 9622.6704
134 | Life-Safety Repairs | WWEQ Basin | The doors for various rooms were propped open and appear to be their normal position. Suspect that ventilation in the room is not adequate. Investigate ventilation and correct as required at waste washwater equalization basin. (LS7) | 35168 | No | 38684.8 | 44846.2857
Notes:
(1) | In 09/17 dollars. Assuming 10% for legal and administration costs.
Note on A42: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B42: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C42: Meghann Chell: Identifies WTP plant system assocaited with task
Note on D42: Meghann Chell: Description of task scope used to develop estimate.
Note on E42: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook. Editable in CIP Full Sheet.
Note on F42: Meghann Chell: YES - Design and Admin Contingency added NO - Only Admin Contingency added Editable in CIP Full Sheet
Note on H42: Meghann Chell: Future value of project based on assumed escalation rate.
Note on I42: Natalie Reilly: Input actual construction cost

## P3
WILLAMETTE RIVER WATER TREATMENT PLANT
CAPITAL IMPROVEMENT PROGRAM UPDATE
PROJECT NO. 3
Project Title |  | Seismic Retrofits
Project Category |  | Risk Mitigation
Project Description |  | The preliminary structural analysis identified both structural and non-structural vulnerabilities that may affect plant performance in a regional catastrophic seismic event. We recommend including seismic retrofits to minimize infrastructure downtime and ensure plant performance after a catastrophic event.
Project Summary Table
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Estimated Task Cost(1) | Future Value in Project Year - Escalation | Actual Construction Cost
86 | Seismic Retrofits | Finished Water Pump Station | The roof joist wall anchorage along the east and west walls of the High Service PS have a DCR of 1.55. Add new wall anchorage along the east and west walls between the existing roof joists. (S3) | 144364 | Yes | 180455 | 209196.8031
87 | Seismic Retrofits | Finished Water Pump Station | The roof diaphragm shear at the High Service PS has a DCR of 1.82 to 2.25. Replace existing deficient deck sections with 16 GA corrugated steel decking. (S4) | 125618 | Yes | 157022.5 | 182032.1133
88 | Seismic Retrofits | Finished Water Pump Station | Tension capacity of the diaphragm chords at the High Service PS has a DCR of 1.20 at connections at the east windows. Strengthen chord splices as required. (S5) | 12159 | Yes | 15198.75 | 17619.5168
89 | Seismic Retrofits | Finished Water Pump Station | Roof deck shear transfer to interior wall ledger bolts at the High Service PS have DCR’s of 3.20 to 3.90. Add new top plate over exterior shear wall and install epoxied anchors. (S6) | 87647 | Yes | 109558.75 | 127008.6185
124 | Seismic Retrofits | Solids - Dewatering | The Solids Handling Building has no lateral load resisting system in the transverse direction at the lower level. Provide structural bracing in the east-west direction by installation of shear wall extensions or exterior steel bracing. (S7) | 47722 | Yes | 59652.5 | 69153.5967
125 | Seismic Retrofits | Solids - Dewatering | The roof joist wall anchorage along the east and west walls of the Solids Handling Building have a DCR of 1.17. Add new wall anchorage along the east and west walls between the existing roof joists. (S8) | 62761 | Yes | 78451.25 | 90946.5002
126 | Seismic Retrofits | Solids - Dewatering | The foundation elements at the Solids Handling Building do not have adequate ties. The floor slab is not doweled into the walls or the footings. Tie the existing slab to the walls with stainless steel angles and epoxy anchors. (S9) | 24672 | Yes | 30840 | 35752.0125
138 | Seismic Retrofits | WWEQ Basin | Waste Washwater EQ Basin North & South Walls: Horizontal reinforcing steel at east corners (#8 @ 12” OC) have a DCR of 1.53 for soil seismic loads. Recommend adding additional reinforced shotcrete to wall or adding three concete/steel braces across the basin. (S1) | 219386 | Yes | 274232.5 | 317910.6276
139 | Seismic Retrofits | WWEQ Basin | Waste Washwater EQ Basin North & South Walls: Wall shear at the concrete beam has a DCR of 1.67 for soil seismic loads. Recommend addition of reinforced shotcrete to wall or addition of concrete/steel braces across the basin. (S2) | 197164 | Yes | 246455 | 285708.892
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
Note on A43: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B43: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C43: Meghann Chell: Identifies WTP plant system assocaited with task
Note on D43: Meghann Chell: Description of task scope used to develop estimate.
Note on E43: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook. Editable in CIP Full Sheet.
Note on F43: Meghann Chell: YES - Design and Admin Contingency added NO - Only Admin Contingency added Editable in CIP Full Sheet
Note on H43: Meghann Chell: Future value of project based on assumed escalation rate.
Note on I43: Natalie Reilly: Input actual construction cost

## P4
WILLAMETTE RIVER WATER TREATMENT PLANT
CAPITAL IMPROVEMENT PROGRAM UPDATE
PROJECT NO. 4
Project Title |  | 30 MGD Expansion
Project Category |  | Capacity Improvement
Project Description |  | To maximize the available space at the WRWTP with the goal of achieving a total capacity of 60 mgd in the existing site boundary, the 30-mgd capacity expansion will be designed based on updated process design criteria for the 20-mgd capacity expansion. This will allow the plant to maximize the available space at the WRWTP with the intention of achieving a total capacity of 60 mgd within the existing site boundary. Additionally, using the uprated criteria will allow the WRWTP to deliver high-quality finished water to the cities of Wilsonville, Sherwood, and any potential distribution partners while minimizing rate increases. The 30 mgd expansion requires the following major construction projects: • One Actiflo® basin. • One ozonation basin. • Two filters. • One 35-foot diameter gravity thickener.
Project Summary Table
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Estimated Task Cost(1) | Future Value in Project Year - Escalation | Actual Construction Cost
3 | 30 MGD Expansion | Actiflo™ | Construct an additional Actiflo basin for the 30 MGD capacity upgrade. With the addition of a third basin, the WRWTP will have three 10 MGD basins and can run two basins at 15 MGD in the event one basin requires maintenance. | 4864843 | Yes | 6081053.75 | 10051055.2924
21 | 30 MGD Expansion | Actiflo™ | Replace the two installed flash mix pumps | 378229 | Yes | 472786.25 | 781443.6339
25 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Replace existing 6,000 gallon LOX storage tank with larger tank (12,000 to 15,000 gallons) to ensure sufficient storage with 20 MGD plant capacity. Recommend purchasing LOX tank (rather than leasing from vendor) so LOX can be purchased from different vendors. | 262500 | Yes | 328125 | 542340.6293
28 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Install a second dry polymer feeder to provide redundancy to plant chemical operations | 240000 | Yes | 300000 | 495854.2897
29 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Install a third 400 PPD ozone generator to support plant capacity expansion | 1193917 | Yes | 1492396.25 | 2466703.6082
30 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Convert hypochlorite system from liquid chemical storage to dry sodium hypochlorite process system for increased storage capacity and plant resiliency. | 637883 | Yes | 797353.75 | 1317904.2578
31 | 30 MGD Expansion | Chemical Storage/ Ozone Generation | Modify existing Chemical Storage Room to increase usable space for existing chemical systems. Recommendations include installation of roll-up door, removal of aqueous ammonia system, modifications necessary to expand hypochlorite system, and modifications to chemical containment to allow additional tanks. | 160350 | Yes | 200437.5 | 331292.6473
60 | 30 MGD Expansion | Filters | Construct two new media filters to support plant expansion to 30 MGD | 4185194 | Yes | 5231492.5 | 8646859.9919
76 | 30 MGD Expansion | Finished Water Pump Station | Upgrade three existing 7.5 MGD finished water pumps with three 12 MGD pumps | 4896098 | Yes | 6120122.5 | 10115629.9833
77 | 30 MGD Expansion | Finished Water Pump Station | Install a fifth finished water pump as part of the 30 MGD upgrade. Recommend 7.5 MGD pump (only valid if not installed during 20 MGD expansion) | 1185023 | Yes | 1481278.75 | 2448328.0747
101 | 30 MGD Expansion | Ozonation | Construct a third ozone basin and gallery to support 30 MGD expansion | 3420955 | Yes | 4276193.75 | 7067896.7148
108 | 30 MGD Expansion | Raw Water Pump Station | Replace two existing 7.5 MGD pumps with 15 MGD pumps | 1772847 | Yes | 2216058.75 | 3662807.4579
118 | 30 MGD Expansion | Solids - Dewatering | Install a third 60 GPM centrifuge and solids transfer pump to support the 30 MGD plant expansion | 1665316 | Yes | 2081645 | 3440642.0095
128 | 30 MGD Expansion | Solids - Gravity Thickener | Construct a second 35-ft diameter gravity thickener to support the 30 MGD plant expansion and provide solids handling redundancy | 870475 | Yes | 1088093.75 | 1798453.1784
132 | 30 MGD Expansion | WWEQ Basin | Install fourth washwater recycle pump for additional redundancy at 30 MGD expansion | 281250 | Yes | 351562.5 | 581079.2457
173 | 30 MGD Expansion | Finished Water Pump Station | Temporary pump station to supply 15 MGD from the WWSP Treatment Plant to the WRWTP distribution system in the event of a service distruption. | 4896098 | Yes | 6120122.5 | 10115629.9833
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
Note on A46: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B46: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C46: Meghann Chell: Identifies WTP plant system assocaited with task
Note on D46: Meghann Chell: Description of task scope used to develop estimate.
Note on E46: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook. Editable in CIP Full Sheet.
Note on F46: Meghann Chell: YES - Design and Admin Contingency added NO - Only Admin Contingency added Editable in CIP Full Sheet
Note on H46: Meghann Chell: Future value of project based on assumed escalation rate.
Note on I46: Natalie Reilly: Input actual construction cost

## P5
WILLAMETTE RIVER WATER TREATMENT PLANT
CAPITAL IMPROVEMENT PROGRAM UPDATE
PROJECT NO. 5
Project Title |  | Operations - Repair & Replace
Project Category |  | Renewal and Replacement
Project Description |  | The WRWTP requires ongoing maintenance/repair and replacement (R&R) of its existing infrastructure to meet service goals. This 2017 MPU summarizes repair and replacement projects for the next 20 years.
Project Summary Table
P# | CIP Project Stage | System Name | CIP - Task Description | Estimated Construction Cost | Design Project? | Estimated Task Cost(1) | Project Completion Year | Future Value in Project Year - Escalation | Actual Construction Cost
10 | Repair & Replace | Actiflo™ | Replace the four hydrocyclones installed in the two existing Actiflo Basins | 318000 | No | 349800 | 2020 | 382235.9046
12 | Repair & Replace | Actiflo™ | Replace lamella settling tubes in the two existing Actiflo basins, which are damaged due to UV exposure. | 245656 | No | 270221.6 | 2020 | 295278.4383
13 | Repair & Replace | Actiflo™ | Upgrade vendor PLC components in the two existing Actiflo basins | 62108 | No | 68318.8 | 2022 | 79200.2136
14 | Repair & Replace | Actiflo™ | Replace the two flash mix pumps (installed and standby) | 188760 | No | 207636 | 2020 | 226889.4634
15 | Repair & Replace | Actiflo™ | Replace the six mixers installed in the two existing Actiflo Basins | 302400 | No | 332640 | 2022 | 385620.9281
16 | Repair & Replace | Actiflo™ | Replace the two sample pumps installed in the two existing Actiflo Basins | 46051 | No | 50656.1 | 2022 | 58724.3034
17 | Repair & Replace | Actiflo™ | Replace original dry polymer batching system (T-13ME01) | 198750 | No | 218625 | 2027 | 293813.7184
18 | Repair & Replace | Actiflo™ | PLC upgrade for Actiflo Local Control Panels | 84000 | No | 92400 | 2027 | 124177.8735
19 | Repair & Replace | Actiflo™ | Replace existing streaming current analyzer on Actiflo inlet | 23500 | No | 25850 | 2036 | 45328.1315
20 | Repair & Replace | Actiflo™ | Replace the five solids pumps (installed and standby) on the existing Actiflo basins | 640000 | No | 704000 | 2036 | 1234468.2614
22 | Repair & Replace | Actiflo™ | Replace the six mixers installed in the two existing Actiflo Basins | 302400 | No | 332640 | 2036 | 583286.2535
23 | Repair & Replace | Actiflo™ | Replace the four hydrocyclones installed in the two existing Actiflo Basins | 369000 | No | 405900 | 2036 | 711748.1069
38 | Repair & Replace | Chemical Storage/ Ozone Generation | Upgrade vendor PLC components in the existing dry polymer blending unit | 22060 | No | 24266 | 2022 | 28130.9447
40 | Repair & Replace | Chemical Storage/ Ozone Generation | Replate two existing 300 PPD ozone generators with 400 PPD units | 1752000 | No | 1927200 | 2022 | 2234152.996
42 | Repair & Replace | Chemical Storage/ Ozone Generation | Inspect existing alum tank and repair as needed | 52500 | No | 57750 | 2022 | 66948.0778
43 | Repair & Replace | Chemical Storage/ Ozone Generation | Inspect existing caustic soda tank and repair as needed | 52500 | No | 57750 | 2022 | 66948.0778
44 | Repair & Replace | Chemical Storage/ Ozone Generation | Replace the LOX evaporator equipment | 112500 | No | 123750 | 2036 | 216996.3741
68 | Repair & Replace | Filters | Replace existing air scour blowers and motors on existing media filtration system | 351000 | No | 386100 | 2022 | 447595.7201
73 | Repair & Replace | Filters | Replace aging MCC in existing filter gallery | 70000 | No | 77000 | 2036 | 135019.9661
74 | Repair & Replace | Filters | Replace air scour blowers and motors on existing media filtration system | 402000 | No | 442200 | 2036 | 775400.3767
83 | Repair & Replace | Finished Water Pump Station | Replace VFDs on three Finished Water Pumps | 596336 | No | 655969.6 | 2019 | 695918.1486
84 | Repair & Replace | Finished Water Pump Station | Replace existing soft-start controller on High Service Pump 3 | 84000 | No | 92400 | 2027 | 124177.8735
85 | Repair & Replace | Finished Water Pump Station | Replace two existing backwash supply pumps in the Wastewater Equalization Basin | 1980000 | No | 2178000 | 2032 | 3393253.0334
92 | Repair & Replace | Miscellaneous | Replace the existing safety and warning signs throughout the site | 15000 | No | 16500 | 2022 | 19128.0222
93 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2020 | 8413.9979
94 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2020 | 5258.7487
95 | Repair & Replace | Miscellaneous | Upgrade site security monitoring system camera and computer | 23500 | No | 25850 | 2020 | 28246.993
96 | Repair & Replace | Miscellaneous | Replace sitewide fire extinguishers | 15000 | No | 16500 | 2022 | 19128.0222
97 | Repair & Replace | Miscellaneous | Replace the two existing irrigation waste pumps (T-30P01/2) | 340000 | No | 374000 | 2022 | 433568.5038
98 | Repair & Replace | Miscellaneous | Replace the two existing water feature pumps (T-30P01/2) | 340000 | No | 374000 | 2027 | 502624.7259
109 | Repair & Replace | Raw Water Pump Station | Replace existing raw water sump pump | 100000 | No | 110000 | 2020 | 120199.97
110 | Repair & Replace | Raw Water Pump Station | Replace osbsolete Robocon VFDs on three Raw Water Pumps | 97375 | No | 107112.5 | 2019 | 113635.6513
111 | Repair & Replace | Raw Water Pump Station | Replace two existing Air Burst Compressors | 395000 | No | 434500 | 2027 | 583931.6668
112 | Repair & Replace | Raw Water Pump Station | Replace existing air burst control panel PLC and local control panel | 42375 | No | 46612.5 | 2027 | 62643.3022
113 | Repair & Replace | Raw Water Pump Station | Replace the existing constant-speed 7.5 MGD pump with a VFD-controlled pump | 682500 | No | 750750 | 2036 | 1316444.6693
117 | Repair & Replace | Sitewide | Replace obsolete ABB magnetic flow meters installed throughout the WRWTP and at Wilsonville Road | 662400 | No | 728640 | 2019 | 773014.176
120 | Repair & Replace | Solids - Dewatering | Replace the existing dewatered sludge screw conveyor in the Solids Handling Building | 87000 | No | 95700 | 2022 | 110942.5289
121 | Repair & Replace | Solids - Dewatering | Replace two existing 60 GPM centrifuges and transfer pumps | 3500000 | No | 3850000 | 2027 | 5174078.0605
122 | Repair & Replace | Solids - Dewatering | Replace existing PLC and local control panel for two dewatering centrifuges | 84000 | No | 92400 | 2027 | 124177.8735
123 | Repair & Replace | Solids - Dewatering | Replace two existing 60 GPM solids transfer pumps | 316059 | No | 347664.9 | 2036 | 609632.5066
129 | Repair & Replace | Solids - Gravity Thickener | Replace two existing sludge mixing pumps (one installed, one shelf spare) | 260000 | No | 286000 | 2020 | 312519.922
130 | Repair & Replace | Solids - Gravity Thickener | Replace the two existing sludge mixing pumps | 260000 | No | 286000 | 2032 | 445578.6811
131 | Repair & Replace | Solids - Gravity Thickener | Replace the existing gravity thickener drive | 114264 | No | 125690.4 | 2036 | 220398.8772
135 | Repair & Replace | WWEQ Basin | Replace three existing filter waste washwater recycle pumps | 300000 | No | 330000 | 2020 | 360599.91
137 | Repair & Replace | WWEQ Basin | Replace three existing filter waste washwater recycle pumps | 43036 | No | 47339.6 | 2036 | 83010.2752
141 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2021 | 8666.4178
142 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2021 | 5416.5111
143 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2022 | 8926.4104
144 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2022 | 5579.0065
145 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2023 | 9194.2027
146 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2023 | 5746.3767
147 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2024 | 9470.0288
148 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2024 | 5918.768
149 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2025 | 9754.1296
150 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2025 | 6096.331
151 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2026 | 10046.7535
152 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2026 | 6279.2209
153 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2027 | 10348.1561
154 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2027 | 6467.5976
155 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2028 | 10658.6008
156 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2028 | 6661.6255
157 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2029 | 10978.3588
158 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2029 | 6861.4743
159 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2030 | 11307.7096
160 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2030 | 7067.3185
161 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2031 | 11646.9409
162 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2031 | 7279.3381
163 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2032 | 11996.3491
164 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2032 | 7497.7182
165 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2033 | 12356.2396
166 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2033 | 7722.6497
167 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2034 | 12726.9268
168 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2034 | 7954.3292
169 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2035 | 13108.7346
170 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2035 | 8192.9591
171 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site fire alarm | 7000 | No | 7700 | 2036 | 13501.9966
172 | Repair & Replace | Miscellaneous | Annual maintenance on the existing site sprinkler system | 4375 | No | 4812.5 | 2036 | 8438.7479
Notes:
(1) | In 09/17 dollars. Assuming 15% contingency for Design and 10% for legal and administration costs.
Note on A11: Meghann Chell: Project number that ties back to estimate source for ease of updating.
Note on B11: Meghann Chell: Project name. Each ties into individual project sheets.
Note on C11: Meghann Chell: Identifies WTP plant system associated with task.
Note on D11: Meghann Chell: Description of task scope used to develop estimate.
Note on E11: Natalie Reilly: Estimated Construction Cost from OPCC and Cost Factoring Workbook.
Note on F11: Meghann Chell: Yes - Design and Admin Contingency added No - Only Admin Contingency added
Note on H11: Meghann Chell: Estimated year that project comes online.
Note on I11: Meghann Chell: Future value of project based on assumed escalation rate.
Note on J11: Natalie Reilly: Input actual construction cost
Note on C47: Meghann Chell: Change to plant-wide?

## Stakeholder Categories
Category | Basis | City of Wilsonville Responsibility | City of Sherwood Responsibility | Caveats | Review Cycle (if applicable)
1 | Contracted Demand - Wilsonville 10 MGD, Sherwood 5 MGD | 66.7% | 33.3%
2 | Contracted Demand - Wilsonville 20.3 MGD, Sherwood 9.7 MGD | 67.7% | 32.3%
Note on C2: Meghann Chell: Enter value from 0 to 100 here
Note on D2: Meghann Chell: Calculated based on the Wilsonville value

## Financial Summary (2017)
Financial Summary - CIP Costs in $2017
PROJECT |  | FY | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | TOTAL
20 MGD Expansion
| Design |  | 0 | 1885516.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1885516.5
| Administration |  | 0 | 419003.6667 | 419003.6667 | 419003.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257011
| Construction |  | 0 | 0 | 6285055 | 6285055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12570110
| Total |  | 0 | 2304520.1667 | 6704058.6667 | 6704058.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15712637.5
Life-Safety Repairs
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administration |  | 0 | 0 | 0 | 28006.95 | 28006.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56013.9
| Construction |  | 0 | 0 | 0 | 0 | 560139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560139
| Total |  | 0 | 0 | 0 | 28006.95 | 588145.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616152.9
Seismic Retrofits
| Design |  | 0 | 0 | 0 | 138223.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138223.95
| Administration |  | 0 | 0 | 0 | 46074.65 | 46074.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92149.3
| Construction |  | 0 | 0 | 0 | 0 | 921493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 921493
| Total |  | 0 | 0 | 0 | 184298.6 | 967567.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151866.25
30 MGD Expansion
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636646.7 | 0 | 0 | 0 | 0 | 0 | 0 | 4636646.7
| Administration |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772774.45 | 772774.45 | 772774.45 | 772774.45 | 0 | 0 | 0 | 3091097.8
| Construction |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10303659.3333 | 10303659.3333 | 10303659.3333 | 0 | 0 | 0 | 30910978
| Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5409421.15 | 11076433.7833 | 11076433.7833 | 11076433.7833 | 0 | 0 | 0 | 38638722.5
Repair & Replace
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administration |  | 0 | 0 | 135611.1 | 144729.1 | 1137.5 | 310899.4 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 473950 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 225137.5 | 1137.5 | 1137.5 | 1137.5 | 308663.4 | 1612640.5
| Construction |  | 0 | 0 | 1356111 | 1447291 | 11375 | 3108994 | 11375 | 11375 | 11375 | 11375 | 4739500 | 11375 | 11375 | 11375 | 11375 | 2251375 | 11375 | 11375 | 11375 | 3086634 | 16126405
| Total |  | 0 | 0 | 1491722.1 | 1592020.1 | 12512.5 | 3419893.4 | 12512.5 | 12512.5 | 12512.5 | 12512.5 | 5213450 | 12512.5 | 12512.5 | 12512.5 | 12512.5 | 2476512.5 | 12512.5 | 12512.5 | 12512.5 | 3395297.4 | 17739045.5
Total |  |  | 0 | 2304520.1667 | 8195780.7667 | 8508384.3167 | 1568226.1 | 3419893.4 | 12512.5 | 12512.5 | 12512.5 | 12512.5 | 5213450 | 12512.5 | 12512.5 | 5421933.65 | 11088946.2833 | 13552946.2833 | 11088946.2833 | 12512.5 | 12512.5 | 3395297.4 | 73858424.65
Stakeholders |  | Resp.
| City of Wilsonville |  | 0 | 1537114.9512 | 5466585.7714 | 5675092.3392 | 1046006.8087 | 2281068.8978 | 8345.8375 | 8345.8375 | 8345.8375 | 8345.8375 | 3477371.15 | 8345.8375 | 8345.8375 | 3670523.956 | 7507091.5088 | 9150579.5088 | 7507091.5088 | 8345.8375 | 8345.8375 | 2264663.3658 | 48112841.5154
| 20 MGD Expansion | 66.7% | 0 | 1537114.9512 | 4471607.1307 | 4471607.1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8943214.2613
| Life Safety Repairs | 66.7% | 0 | 0 | 0 | 18680.6357 | 392293.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410973.9843
| Seismic Retrofits | 66.7% | 0 | 0 | 0 | 122927.1662 | 645367.6226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768294.7888
| 30 MGD Expansion | 67.7% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3662178.1185 | 7498745.6713 | 7498745.6713 | 7498745.6713 | 0 | 0 | 0 | 26158415.1325
| Repair & Replace | 66.7% | 0 | 0 | 994978.6407 | 1061877.4067 | 8345.8375 | 2281068.8978 | 8345.8375 | 8345.8375 | 8345.8375 | 8345.8375 | 3477371.15 | 8345.8375 | 8345.8375 | 8345.8375 | 8345.8375 | 1651833.8375 | 8345.8375 | 8345.8375 | 8345.8375 | 2264663.3658 | 11831943.3485
| City of Sherwood |  | 0 | 767405.2155 | 2729194.9953 | 2833291.9774 | 522219.2913 | 1138824.5022 | 4166.6625 | 4166.6625 | 4166.6625 | 4166.6625 | 1736078.85 | 4166.6625 | 4166.6625 | 1751409.6939 | 3581854.7745 | 4402366.7745 | 3581854.7745 | 4166.6625 | 4166.6625 | 1130634.0342 | 23441062.968
| 20 MGD Expansion | 33.3% | 0 | 767405.2155 | 2232451.536 | 2232451.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4464903.072
| Life Safety Repairs | 33.3% | 0 | 0 | 0 | 9326.3143 | 195852.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205178.9157
| Seismic Retrofits | 33.3% | 0 | 0 | 0 | 61371.4338 | 322200.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383571.4612
| 30 MGD Expansion | 32.3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1747243.0314 | 3577688.112 | 3577688.112 | 3577688.112 | 0 | 0 | 0 | 12480307.3675
| Repair & Replace | 33.3% | 0 | 0 | 496743.4593 | 530142.6933 | 4166.6625 | 1138824.5022 | 4166.6625 | 4166.6625 | 4166.6625 | 4166.6625 | 1736078.85 | 4166.6625 | 4166.6625 | 4166.6625 | 4166.6625 | 824678.6625 | 4166.6625 | 4166.6625 | 4166.6625 | 1130634.0342 | 5907102.1515
Notes
1 | For 20 MGD Expansion, Life Safety Repairs, Seismic Retrofits, and 30 MGD Expansion projects, all design costs were assumed to be in the first year of the project and the construction costs were split over the remaining project years.
2 | For the Repair and Replace projects, the design and construction costs were assumed to be in the project completion year.
Note on C29: Natalie Reilly: The percent responsibility for each stakeholder is stipulated on the ReadMe sheet. Change the percent in this column to hard-enter another value for one of the projects.

## Financial Summary (Future)
Financial Summary - CIP Costs in Projected Future Dollars
PROJECT |  | FY | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | TOTAL
20 MGD Expansion
| Design |  | 0 | 2124423.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2124423.0551
| Administration |  | 0 | 472094.0122 | 472094.0122 | 472094.0122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1416282.0367
| Construction |  | 0 | 0 | 7081410.1836 | 7081410.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14162820.3672
| Total |  | 0 | 2596517.0673 | 7553504.1958 | 7553504.1958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17703525.459
Life-Safety Repairs
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administration |  | 0 | 0 | 0 | 32467.731 | 32467.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64935.4621
| Construction |  | 0 | 0 | 0 | 0 | 649354.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 649354.6207
| Total |  | 0 | 0 | 0 | 32467.731 | 681822.3517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714290.0828
Seismic Retrofits
| Design |  | 0 | 0 | 0 | 160239.4417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160239.4417
| Administration |  | 0 | 0 | 0 | 53413.1472 | 53413.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106826.2945
| Construction |  | 0 | 0 | 0 | 0 | 1068262.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1068262.9445
| Total |  | 0 | 0 | 0 | 213652.5889 | 1121676.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1335328.6807
30 MGD Expansion
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7663670.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 7663670.5198
| Administration |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1277278.42 | 1277278.42 | 1277278.42 | 1277278.42 | 0 | 0 | 0 | 5109113.6799
| Construction |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17030378.9328 | 17030378.9328 | 17030378.9328 | 0 | 0 | 0 | 51091136.7985
| Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8940948.9397 | 18307657.3528 | 18307657.3528 | 18307657.3528 | 0 | 0 | 0 | 63863920.9981
Repair & Replace
| Design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Administration |  | 0 | 0 | 143869.816 | 158149.3953 | 1280.2663 | 360417.6141 | 1358.2345 | 1398.9815 | 1440.951 | 1484.1795 | 636949.168 | 1574.566 | 1621.803 | 1670.4571 | 1720.5708 | 350756.8893 | 1825.3536 | 1880.1142 | 1936.5176 | 541243.1403 | 2210578.0179
| Construction |  | 0 | 0 | 1438698.1599 | 1581493.9526 | 12802.6627 | 3604176.1414 | 13582.3449 | 13989.8152 | 14409.5097 | 14841.795 | 6369491.6799 | 15745.6603 | 16218.0301 | 16704.571 | 17205.7081 | 3507568.8925 | 18253.5357 | 18801.1418 | 19365.1761 | 5412431.4026 | 22105780.1795
| Total |  | 0 | 0 | 1582567.9759 | 1739643.3478 | 14082.929 | 3964593.7555 | 14940.5794 | 15388.7967 | 15850.4606 | 16325.9745 | 7006440.8479 | 17320.2263 | 17839.8331 | 18375.0281 | 18926.2789 | 3858325.7818 | 20078.8893 | 20681.256 | 21301.6937 | 5953674.5429 | 24316358.1974
Total |  |  | 0 | 2596517.0673 | 9136072.1717 | 9539267.8636 | 1817581.3725 | 3964593.7555 | 14940.5794 | 15388.7967 | 15850.4606 | 16325.9745 | 7006440.8479 | 17320.2263 | 17839.8331 | 8959323.9678 | 18326583.6317 | 22165983.1346 | 18327736.2421 | 20681.256 | 21301.6937 | 5953674.5429 | 107933423.418
Stakeholders |  | Resp.
| City of Wilsonville |  | 0 | 1731876.8839 | 6093760.1385 | 6362691.665 | 1212326.7755 | 2644384.0349 | 9965.3664 | 10264.3274 | 10572.2572 | 10889.425 | 4673296.0455 | 11552.5909 | 11899.1687 | 6065278.5759 | 12406907.8559 | 14967787.3243 | 12407676.647 | 13794.3978 | 14208.2297 | 3971100.9201 | 70898355.7459
| 20 MGD Expansion | 66.7% | 0 | 1731876.8839 | 5038187.2986 | 5038187.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10076374.5972
| Life Safety Repairs | 66.7% | 0 | 0 | 0 | 21655.9766 | 454775.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476431.4852
| Seismic Retrofits | 66.7% | 0 | 0 | 0 | 142506.2768 | 748157.9532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890664.23
| 30 MGD Expansion | 67.7% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6053022.4322 | 12394284.0278 | 12394284.0278 | 12394284.0278 | 0 | 0 | 0 | 43235874.5157
| Repair & Replace | 66.7% | 0 | 0 | 1055572.8399 | 1160342.113 | 9393.3136 | 2644384.0349 | 9965.3664 | 10264.3274 | 10572.2572 | 10889.425 | 4673296.0455 | 11552.5909 | 11899.1687 | 12256.1437 | 12623.828 | 2573503.2965 | 13392.6192 | 13794.3978 | 14208.2297 | 3971100.9201 | 16219010.9177
| City of Sherwood |  | 0 | 864640.1834 | 3042312.0332 | 3176576.1986 | 605254.597 | 1320209.7206 | 4975.2129 | 5124.4693 | 5278.2034 | 5436.5495 | 2333144.8023 | 5767.6354 | 5940.6644 | 2894045.3919 | 5919675.7758 | 7198195.8103 | 5920059.5951 | 6886.8582 | 7093.464 | 1982573.6228 | 34438550.6048
| 20 MGD Expansion | 33.3% | 0 | 864640.1834 | 2515316.8972 | 2515316.8972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5030633.7944
| Life Safety Repairs | 33.3% | 0 | 0 | 0 | 10811.7544 | 227046.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237858.5976
| Seismic Retrofits | 33.3% | 0 | 0 | 0 | 71146.3121 | 373518.1386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444664.4507
| 30 MGD Expansion | 32.3% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2887926.5075 | 5913373.325 | 5913373.325 | 5913373.325 | 0 | 0 | 0 | 20628046.4824
| Repair & Replace | 33.3% | 0 | 0 | 526995.136 | 579301.2348 | 4689.6154 | 1320209.7206 | 4975.2129 | 5124.4693 | 5278.2034 | 5436.5495 | 2333144.8023 | 5767.6354 | 5940.6644 | 6118.8844 | 6302.4509 | 1284822.4853 | 6686.2701 | 6886.8582 | 7093.464 | 1982573.6228 | 8097347.2797
Notes
1 | For 20 MGD Expansion, Life Safety Repairs, Seismic Retrofits, and 30 MGD Expansion projects, all design costs were assumed to be in the first year of the project and the construction costs were split over the remaining project years.
2 | For the Repair and Replace projects, the design and construction costs were assumed to be in the project completion year.
Note on C29: Natalie Reilly: The percent responsibility for each stakeholder is stipulated on the ReadMe sheet. Change the percent in this column to hard-enter another value for one of the projects.

## List Reference (hidden)
Revised Estimate | Yes | 1
ENR | No | 2
Escalation |  | 3
4
5
6
7
8
9
10